| Holtec Britain Ltd. SMR-300 Generic Design Assessment Resolution Plan for RO-SMR300-006 |  |  |
| --- | --- | --- |
| RO Title: | Design assessment approach for the containment structure |  |
| Revision: | Rev. 0 |  |
| RO Planned Closure Date: |  | Subject to final submissions, see schedule |
| Reference Documentation Related to Regulatory Observation |  |  |
| Regulatory Queries | RQ-01677 |  |
| Linked ROs | RO-Holtec SMR-300-007 |  |
| Other Documentation | - |  |

Scope of work

The SMR-300 is an advanced Pressurised Water Reactor (PWR) Nuclear Power Plant designed by Holtec International, drawing on decades of operational experience to deliver clean, affordable power with enhanced passive safety features. The SMR-300 is designed to meet US regulatory standards and the EPRI Advanced Light Water Reactor Utility Requirements Document, aligning with internationally recognised codes and practices. Holtec judges US and UK regulatory expectations to share a common foundation, shaped by international cooperation and IAEA safety standards. While broad engineering principles are similar in both countries, Holtec acknowledges potential differences in specific regulatory details. The primary focus of a two-step UK Generic Design Assessment (GDA) is for the fundamental adequacy of the SMR-300 to be assessed against UK regulatory expectations. Early in GDA, Holtec established a Design Reference Point (DRP) based on the SMR-300 design for Palisades in the US. The DRP has been evaluated for compliance with UK regulations and helps identify areas where US and UK requirements may diverge. Ensuring design stability across a global SMR-300 fleet is central to Holtec’s deployment strategy, making the GDA process a critical milestone. The actions, deliverables and schedule produced herein are applicable to UK SMR-300 deployment to meet UK licensing expectations. There is no inherent dependency on these deliverables to support US licensing activities. Background The SMR-300 design provides multiple physical barriers to the release of radioactivity to the environment. These include the fuel cladding, the reactor coolant pressure boundary, and the containment structure (CS). For most light water reactor designs, including the SMR-300, a containment structure is provided in the design to prevent unacceptable releases of radioactivity to the public and the environment following any design basis or beyond design basis accident. The containment of the SMR-300 is designed to remain intact and sealed during all postulated events, and in certain fault scenarios is designed to reject its internal energy to the large body of water surrounding the CS, referred to as the Annular Reservoir (AR), shown in Figure 1. Steel-Concrete Containment Enclosure Structure Annular Reservoir Metallic Containment Structure Figure 1 – High Level Diagram of the Containment Structure (representative of prospective design change) The AR acts as the Ultimate Heat Sink (UHS) for the reactor’s engineered safety systems and alongside the steel CS wall, forms part of the Passive Containment Heat Removal System (PCH). After a postulated event, such as a Loss of Cooling Accident (LOCA), the plant is designed to automatically achieve and maintain a safe shutdown state without operator actions, without external water, without external power and without active systems. Nearly all historical nuclear incidents feature human errors or dependence on active systems, as either a causal or contributing factors. The SMR-300 AR reservoir and CS design address many such issues common to PWR technology, and provide significant risk reduction benefits. The CS and AR design has been developed to ensure it can robustly deliver its safety functions throughout its operational life. In addition, the CS mechanical design needs to be sufficiently robust to both perform its safety functions under any anticipated environmental conditions and to ensure the risk of any inherent hazard from the presence of a large volume of water surrounding the CS, is reduced to ALARP. Engineered Safety Features (ESFs) usually come with a trade-off that needs to be understood in their balance of risk and benefit. The CS and AR design has been developed from the initiation of the SMR-300 to be cognisant of this balance, with the final design still subject to substantiation and optimisation within the detailed design phase. During GDA Step 2, Holtec produced a dedicated reference, the Containment Structure System Based View, to support demonstration of the integrity of the CS. This reference [1] - Identifies claims relevant to the demonstration of integrity of the CS. - Describes the CS in sufficient detail to enable the claims and the supporting arguments to be understood. - Presents the initial safety functional requirements relevant to the demonstration of integrity of the SMR-300 CS. - Identifies the preliminary classification of the CS and justification of the chosen codes and standards. - Presents the current design basis of the CS against the available evidence at GDA Step 2, supporting an initial design basis assessment against the applicable codes and standards. - Provides an initial judgement if the contribution to nuclear safety risk from the CS can be demonstrated to be As Low As Reasonably Practicable (ALARP), based on the fundamental design and planned future activities. Holtec recognised in [1] and in PSR Chapter 20 [2], that there is further work to undertake to fully substantiate the adequacy of the CS design for UK deployment and demonstrate that associated risks are reduced to ALARP. Holtec’s resolution of the Regulatory Observation is aligned with this planned work set out in [1] and is explained below.

- Description of deliverables

RO-Holtec SMR-300-006.A1 – Justification for RP’s approach to component categorisation and classification In response to this Regulatory Observation Action, the RP should: - Action A1.1: demonstrate that the approach to classification of the CS is consistent with ONR expectations described above. - Action A1.2: demonstrate that the classification of the coating is consistent with ONR expectations with regards to auxiliary components. Response Holtec has raised commitment C_FAUL_103 (refer to PSR Chapter B14 [3]) which commits to a comprehensive approach to safety analysis and will appropriately address regulatory expectations and good practice. This commitment is planned to be delivered as part of the development of a Pre-Construction Safety Report (PCSR). Supporting this work, the Containment Structure System Based View provided a preliminary discussion on UK equivalent classification of the CS and its coating, to support a fundamental assessment, recognising that adoption of a UK aligned classification approach is typically a post-Step 2 activity for designs developed outside of the UK. This deliverable will be updated for PCSR, as a tier-2 reference to the safety report, to summarise the safety case for the CS and address the actions listed above. Inputs to the updated Containment Structure System Based View will be taken from analysis or substantiation produced for the safety assessment of the SMR-300 in the United States and from any supplemental assessments performed for a prospective deployment in the UK Which will demonstrate that the CS will withstand all design basis loadings with adequate margin. Whilst the totality of initiating events and their assessment will be presented and managed through the safety analysis topics (Design Basis Analysis, Probabilistic Safety Assessment, Hazard studies etc), the updated Containment Structure System Based View will summarise those relevant to the CS. Resolution of GDA Commitment C_Faul_103 will produce a comprehensive set of Initiating Events through fault identification techniques, such as Failure Modes and Effect Analysis (FMEA) or Hazards and Operability (HazOp) studies. This will build on the initiating events identified in the PSR [4] and take account of any design development since the issue of the design reference point. For the CS, a dedicated CS Failure Modes Study will also be undertaken, to determine any credible failure mechanisms for the CS. This will aim to demonstrate that all possible failure modes within the design basis, including the potential for gross failure, common cause and common mode failures have been considered and identified (Noting that the CS is being designed to withstand design basis loadings, and therefore the likelihood of any failures is extremely unlikely). Any identified types of failures will be a key input into the Hazard studies (noting the consequential hazards assessment is covered in further detail in RO-HOLTECSMR300-007). The scope of the updated Containment Structure System Based View, will therefore include: - A summary of the initiating events originating from and reliant on the CS. - A summary of the safety functions performed by the CS and their categorisation. - A summary of the deterministic and probabilistic assessments of the initiating events and their consequences, including assessment of dependencies (e.g. CCF/CMF) and internal or external hazards. Confirmation of the classification of the CS (and the classification of the coating) will follow within the updated Containment Structure System Based View, based upon the outputs of the above work. Table 1 summarises the key deliverables and safety studies expected to be produced in support of resolution of this action with the highlighted entries indicating those which are needed to close the action. Table 1: Summary of deliverables and safety studies supporting resolution of RO-HOLTECSMR300-006 .A1 Preliminary Title; Description. Containment Structure System Based View (update); Head document summarising the golden thread of the CS throughout the safety case, including any specific arguments and contribution to overall risk.. Containment Structure Failure Modes Study (new); This study will demonstrate that all possible failure modes within the design basis, including the potential for gross failure, common cause and common mode failures have been considered and identified for the CS.. Preliminary Fault Schedule (update); The Preliminary Fault Schedule will be developed and updated to provide a schedule of initiating events and bounding initiating events mapped against claimed safety functions and safety measures.. Safety Assessment Handbook (update); An update to the Safety Assessment Handbook [5] provided as part of GDA. This document will provide the methodology, or reference the detailed methodology, for conservative approach to the deterministic assessment of plant faults, internal hazards and external hazards.. Design Basis Accident Analysis (DBAA) (update); These studies will provide the results of the deterministic assessment of design basis faults, to the methodology and principles described in the Safety Assessment Handbook. These DBAA will be developed from the DBAA produced during GDA [6].. Accident Sequence Analysis of Design Basis Faults (update); These studies will provide the detailed transient analysis of design basis faults, including fault progression, safety system initiation and outputs of RELAP5-3D analysis.. Radiological Consequences Analysis of Design Basis Faults (new); These studies will provide the radiological consequence analysis of design basis faults and comparison with relevant safety limits and targets.. Individual and Combined Internal / External Hazard Assessments (new); These studies will provide the detailed assessment of Hazards originating from or impacting the SMR-300 Engineered Safety Features. RO-Holtec SMR-300-006.A2 – Design of the Containment Structure In response to this Regulatory Observation Action, the RP should demonstrate the adequacy of the Containment Structure design, including how its assessment methodology will address the stability of the Containment Structure, anchoring and other manufacture, inspection and corrosion aspects which are relevant to the SMR-300 design. Response The Containment Structure System Based View [1] provides a preliminary justification of the choice of appropriate codes and standards for the CS and its adequacy of design. The report identified that further work will be undertaken outside of GDA timescales to assess requirements that are specific to the SMR-300 containment structure design. This further work included design requirements relating to manufacture, inspection and corrosion aspects but will be expanded to include: - stability, - anchoring, - wider industry experience from similar vessels or structures, and - the potential failure modes considered in the Action A1 deliverable CS Failure Modes Study. The justification in [1] will be revisited and consider the conclusion of the further work areas identified above. Should any gaps or additional requirements be identified these shall be managed through the Design Decision and Risk Management procedure [7] and the associated risk shown to be as low as is reasonably practicable. The enhanced justification will be reported in an update to the Containment Structure System Based View with lower tier documentation providing detailed assessments, as necessary. In particular, this update will ensure appropriate further consideration of the following aspects, which may require specific studies to investigate these areas: - Additional brittle fracture and thermal shock assessments and justification: to provide additional assurance against the exemption from post-weld heat treatment (accepted for US reactors via ASME Code Case N841) and to support an ALARP position. Note that this work, although not required for US licensing activities, is also covered by GDA Commitment C_Civi_092. - Degradation management of the CS/AR: to provide additional assurance and optioneering that design and coating choices to manage degradation due to the AR aqueous environment ensure risks are reduced to ALARP. Note that this work is also covered by GDA Commitment C_Civi_093. The lower tier deliverables contributing to the resolution of this action and feeding into the Containment Structure System Based View are summarised in Table 2 with highlighted entries indicating those needed to close the action: Table 2: Summary of deliverables and safety studies supporting resolution of RO-HOLTECSMR300-006.A2 Preliminary Title; Description. Containment Structure System Based View (update); Head document summarising the golden thread of the CS throughout the safety case, including any specific arguments and contribution to overall risk.. Containment Structure Failure Modes Study (new); This study will demonstrate that all possible failure modes within the design basis, including the potential for gross failure, common cause and common mode failures have been considered and identified for the CS.. Brittle fracture and thermal shock assessment study (new); To provide additional assurance that the exemption of the CS from post-weld heat treatment (ASME Code Case N841) reduced risks to ALARP.. Further Options study for Degradation management of the CS/AR study (new); To provide additional assurance and optioneering that design choices to manage degradation due to the AR aqueous environment reduced risks to ALARP..

Key Deliverables and Timeline

Deliverables in italics and bold will be formally issued to the ONR to address the actions raised in the Regulatory Observation. Note: T-0 marks the start of PCSR authoring; each earlier “T-n” step represents roughly three months before that start date. Blue cells indicate the periods during which work on each task is scheduled; completion of earlier tasks feeds into subsequent ones.

Impact on GDA submissions

Implementation of this resolution plan will be outside of the GDA timescales and will likely support further development of a PCSR. One GDA submission is affected by this Resolution Plan; Containment Structure System Based View [1] which will be revised, however there is no plan to reissue this document to support GDA Step 2 timescales.

References

# References [1]; Holtec Britain, “HI-2250348, Containment Structure System Based View,” Revision 0, May 2025.”.. [2]; Holtec Britain, “HI-2240357, Holtec SMR GDA PSR Part B Chapter 20 Civil Engineering, Revision 1, July 2025”.. [3]; Holtec Britian, “HI-2240345 R1, HOLTEC SMR GDA PSR Part B Chapter 14, Safety/Design Basis Accident Analysis,” 2025.. [4]; Holtec Britain, “HI-2241323 R0, Preliminary Fault Schedule Report,” 2024.. [5]; Holtec Britain, “SMR-300 GDA Safety Assessment Handbook,” 2025.. [6]; “HI-2241577 R0, SMR-300 GDA UK DBAA Summary Report,” 2025..