ONR Assessment Report Generic Design Assessment of the Rolls-Royce SMR – Step 2 Human Factors

ONR Assessment Report

Project Name: Generic Design Assessment of the Rolls-Royce SMR

Report Title: Step 2 Human Factors

Authored by: [Redacted]

Report Issue No: 1

Document ID: ONRW-2126615823-3678

Publication Date: Jun-24

© Office for Nuclear Regulation, 2024

For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled. If you wish to reuse this information visit www.onr.org.uk/copyright for details.

# Executive Summary

This report presents the outcomes of my Human Factors assessment of the Rolls-Royce Small Modular Reactor (SMR) as part of Step 2 of the Office for Nuclear Regulation (ONR) Generic Design Assessment (GDA). This assessment is based upon the information presented in version 2 of Rolls-Royce SMR Limited’s Environmental, Safety, Security and Safeguards (E3S) case chapters and supporting documentation.

ONR’s GDA process calls for a step-wise assessment, which increase in detail as the project progresses. The focus of my assessment in this step was towards the fundamental adequacy of the Rolls-Royce SMR design and safety case, and the suitability of the methodologies, approaches, codes, standards and philosophies which form the building blocks for the design and generic safety and security cases.

I targeted my assessment, in accordance with my assessment plan, at the content of most relevance to Topic against the expectations of ONR’s Safety Assessment Principles (SAPs), Technical Assessment Guides (TAGs) and other guidance which ONR regards as relevant good practice.

I targeted the following aspects in my assessment of the Rolls-Royce SMR E3S case:

- The adequacy of the HF Integration (HFI) on the project. My focus was on nuclear safety, but it did include whether the Requesting Party had within its HFI scope the recognition that HF is applicable to Conventional Health and Safety, Environment, Security, and Safeguards (E3S).

- The suitability of the allocation of nuclear safety functions between the human and technology.

- The adequacy of the HF engineering programme.

- The adequacy of the Requesting Party’s (RP’s) approach to the Identification, Analysis and Substantiation of Human Based claims.

- The adequacy of the HF safety case and design analysis submissions.

- The  suitability of the  concept of operations as it currently stands.

The conclusions of my assessment comprise:

- There are no fundamental issues identified to date with the HF elements of the: process and organisational enablers for HFI, the Rolls-Royce SMR design, and the E3S case, that I conisder to be prejudicial to the RP entering Step 3.

- The Rolls-Royce SMR design features very few novel concepts that are likely to challenge the ability of the operator to safely and securely operate it. The ‘small’ characteristic of an SMR design could pose a risk to EMIT (Examination Maintenance Inspection Testing) activities due to the reduced plant footprint, but in recognition of this risk, the RP has introduced advanced human Computer Aided Design (CAD) tools to identify and design out (or mitigate) contested space.

- In terms of capability, I consider the RP’s HF team to be suitably competent to have developed a modern standards HFI programme for Step 2. The RP is committed to securing additional resource for Step 3 and I will monitor delivery progress and quality as a residual matter.

- I consider the scope of HFI for nuclear safety to meet Relevant Good Practice (RGP). However, at Step 2, the RP has provided insufficent material to conclude the same for HFI scope in the following domains: Conventional Health and Safety; Security; Safeguards and Environment. The RP recognises that further work in these domains is required and I will monitor progress in the RP’s scope development during Step 3 as residual matters. Assessing application of HF in these areas during Step 3 is outside of my assessment scope, but I will raise the need for this with ONR’s assessment leads and with inspectors in the respective areas.

- I consider that the methods and approaches that the RP has put in place for suitable and sufficient HFI meet, are close to meeting, or exceed, RGP. The RP is aware of those areas where further work is required and is actively working on these during the final stages of Step 2 and where necessary will be taking them forward as part of Step 3. I will monitor progress during Step 3 as a residual matter.

- I consider the HF RGP selected for the Rolls-Royce SMR design broadly meets regulatory expectations but note that further work is required in this area as it is currently incomplete; especially in the area of identifying specific legal requirements such as Lifting Operations and Lifting Equipment Regulations (LOLER) and Provision and Use of Work Equipment Regulations (PUWER), and regime-specific legal requirements and approaches in the areas of Secuirty, Safegaurds and Environment. The RP recognises these shortfalls and is updating the design guidance, which will be reissued during Step 3. I will follow this up during Step 3 as a residual matter to ensure that the RGP selected supports the demonstration of ALARP for nuclear safety (as far as is practicable within GDA). The suitability of HF RGP for the non-nuclear safety domains will be outside of my Step 3 assessment. This will be assessed by the Environment Agencies (EA) and other ONR disciplines.

- Whilst the HFI enablers generally meet RGP, the evidence that the arangemnets are being used as intended does not fully support the primary E3S claim that, “Human Factors is integrated into the design based on sound safety principles and methods that minimise risks to ALARP”. I found several shortfalls in expectations with respect to HF representation in optioneering and design reviews which RR have committed to address moving forward.

- The RP has established a suitable approach to determine an optimised balance between engineered systems and human delivery of functions – noting that evidence of application to Environment, Security and Safegaurd domains was not submitted in Step 2. I will monitor the inclusion of the full scope of the E3S in the Allocation of Function (AoF) process during Step 3, but my focus will remain nuclear safety. Other disciplines will consider the adequacy of the AoF decision making for their areas. I will also sample a range of AoF decisions to ensure that they have adequately followed the RP’s declared process, and any subsequent HFE work supporting the implementation of the function.

- The RP has established a generally suitable approach for the identification of Human Based Safety Claims (HBSCs). Further, there is evidence that these are being captured in both the Probabilistic Safety Assessment (PSA) and the Fault Schedule. However, I note an over-classification of HBSCs such that the RP is reporting an extremely high number of Class 1 operator claims for at power operations. The RP recognises this and will be revising its approach early in Step 3. I will monitor progress in this area during Step 3 as a residual matter.

- Human Reliability Analysis (HRA) data currently used is based on simplistic, but conservative, screening Human Error Probabilities (HEPs), and US sourced Iniating Event Frequency (IEF) data. Given the design maturity I consider this appropriate but note it will need significant work in this area to be considered a) best estimate, and b) part of a suitable and sufficient risk assessment that includes propportionate task and error analysis, comprises all error types (inc. errors of commission), and appropriately considers violations. I will monitor progress in this area during Step 3 as a residual matter.

- The RP has established generally suitable approaches for Human Factors Engineering (HFE), but there is evidence that these systems are not being adequately applied by non HF Suitably Qualified and Experienced Person/s (SQEPs). I will follow this up during Step 3 as a residual matter.

- The RP has provided insufficient evidence at Step 2 that the scope, and incorporation within the design, of Operational Experience (OPEX) and Learning within the HF domain is adequate. I note that the RP is aware of this and has been carrying out remedial work during Step 2. I will follow this up during Step 3 as a residual matter.

Overall, based on my assessment to date, and subject to the provision and assessment of suitable and sufficient supporting evidence, I have not identified any fundamental safety shortfalls that could prevent ONR permissioning the construction of a power station based on the generic Rolls-Royce SMR design.

# List of Abbreviations

ALARP	As Low As Reasonably Practicable

AoF		Allocation of Function

APJ		Absolute Probability Judgement

BSL		Basic Safety level (in SAPs)

BSO		Basic Safety Objective (in SAPs)

CAE		Claim/s Arguments Evidence

CDF		Core Damage Frequency

CDM		Construction Design and Manufacture

CH&S		Conventional Health and Safety

CNS		Civil Nuclear Security (ONR)

DAC		Design Acceptance Certificate

DiD		Defence in Depth

DSA		Deterministic Safety Analysis.

DOORS	Dynamic Object Oriented Requirements System

EA		Environment Agency

EEMUA	Engineering Equipment and Materials Users Association

EMIT		Examination Maintenance Inspection Testing

E3S		Environment, Safety, Security and Safeguards

GDA		Generic Design Assessment

HAZID	Hazard Identfication (Studies)

HAZOPS 	Hazard and Operability Studies

HBSCs 	Human Based Safety Claims

HEPs		Human Error Probabilities

HEART 	Human Error Analysis Reliability Technique

HF		Human Factors

HFE		Human Factors Engineering

HFI 		Human Factors Integration

HOW2	ONR’s Management System internal online portal

HRA		Human Reliability Assessment

HSE		Health and Safety Executive

HTA		Hierarchical Task Analysis

IAEA		International Atomic Energy Agency

IEF		Initiating Event Frequency/ies

IOSH		Institute of Occupational Safety and Health

ISV		Integrated System Validation (trials)

LC		Licence Condition

LOLER	Lifting Operations and Lifting Equipment Regulations

NRW		Natural Resources Wales

ONR		Office for Nuclear Regulation

OPEX		Operational Experience

OSD		Operational Sequence Diagrams

PCER		Pre-construction Environnent Report

PCSR		Pre-construction Safety Report

PIEs		Postulated Initiating Event/s

PSA		Probabilistic Safety Assessment

PUWER	Provision and Use of Work Equipment Regulations

PWR		Pressurised Water Reactor

RAIDO	Risks, Assumptions, Issues, Dependencies and Opportunities

RR		Rolls-Royce

RGP		Relevant Good Practice

SAA		Severe Accident Analysis

SAP		Safety Assessment Principle(s)

SFAIRP	So far as is reasonably practicable

SMR		Small Modular Reactor

SPAR-H	Standardised Plant Analysis Risk – HRA

SSCs		Structure, System and Component/s

SQEPs	Suitably Qualified and Experienced Person/s

SWIFT 	Structured What If Technique

TAG		Technical Assessment Guide(s) (ONR)

THERP 	Technique for Human Error Rate Prediction

TINS		Tasks Important to Nuclear Security

TSC		Technical Support Contractor

TTA 		Tabular Task and Error Analysis

V&V		Verification and Validation

VAI 		Vital Area Assessment

WENRA	Western European Nuclear Regulators’ Association

Contents

Executive Summary	3

List of Abbreviations	7

1.	Introduction	10

2.	Assessment standards and interfaces	12

3.	Requesting party’s submission	15

4.	ONR assessment	21

5.	Conclusions	57

References	60

Appendix 1 – Relevant SAPs considered during the assessment	64

Appendix 2 – HF HAZOP / SWIFT attendance	65

# Introduction

- This report presents the outcomes of my Human Factors (HF) assessment of the Rolls-Royce Small Modular Reactor (SMR) as part of Step 2 of the Office for Nuclear Regulation (ONR) Generic Design Assessment (GDA). This assessment is based upon the information presented in version 2 of Rolls-Royce SMR Limited’s Environmental, Safety, Security and Safeguards (E3S) case chapters (refs [1], [2], [3], [4]) and supporting documentation.

- Assessment was undertaken in accordance with the requirements of the Office for Nuclear Regulation (ONR) Management System and follows ONR’s guidance on the mechanics of assessment, NS-TAST-GD-096 (ref. [5]). The ONR Safety Assessment Principles (SAPs) (ref. [6]), together with supporting Technical Assessment Guides (TAGs) (ref. [7]), have been used as the basis for this assessment.

- This is a Major report (refer to NS-TAST-GD-108 (ref. [8])).

  - Background

- The ONR’s GDA process (ref. [9]) calls for a step-wise assessment of the Requesting Party's (RP) submissions with the assessments increasing in detail as the project progresses. Rolls-Royce SMR Limited is the RP for the GDA of the Rolls-Royce SMR design.

- In April 2022 ONR, together with the Environment Agency (EA) and Natural Resources Wales (NRW), began Step 1 of the GDA for the generic Rolls-Royce SMR design. Step 1, which is the preparatory part of the design assessment process and mainly associated with initiation of the project and preparation for technical assessment in later steps, was successfully completed in 12 months.

- Step 2 commenced in April 2023. This is the first substantive technical assessment step. The focus of ONR’s assessments in this step is towards the fundamental adequacy of the design and safety and security cases, and the suitability of the methodologies, approaches, codes, standards and philosophies which form the building blocks for the design and generic safety and security cases. The objective is to undertake an assessment of the design against regulatory expectations to identify any fundamental safety or security shortfalls that could prevent ONR permissioning the construction of a power station based on the design.

- Prior to the start of Step 2, I prepared a detailed Assessment Plan for HF (ref. [10]). This has formed the basis of this assessment and was also shared with the RP to maximise openness and transparency.

- This report is one of a series of Assessments which support ONR’s overall judgements at the end of Step 2 which are recorded in the Step 2 Summary Report (ref. [11]).

  - Scope

- The assessment documented in this report is based upon the E3S case for the Rolls-Royce SMR as summarised in the E3S case chapters and supporting documentation.

- The overall scope of the Rolls-Royce SMR GDA is described in (ref. [12]). Rolls-Royce SMR Limited has indicated that it intends to complete a three step GDA, with the objective of receiving a Design Acceptance Certificate (DAC) from ONR and has aligned their GDA scope with this objective. The GDA scope defines the generic plant and layout and includes all systems, structures and components that are identified as being important to safety, security and safeguards, all modes of operation, and all stages of the plant lifecycle.

- However, given the step-wise assessment during GDA, information has not been submitted for all aspects within the GDA Scope during Step 2. The following aspects of the E3S case are therefore out of scope of this assessment:

- Whilst I have assessed whether the RP has included the full E3S case within the its HFI scope, I have only considered the application of HF with respect to nuclear safety in this assessment report. The application of HF in support of Conventional Health Safety, Environment, Security and Safeguards is assessed within those assessment reports.

- My assessment has considered the following aspects:

- The adequacy of the Human Factors Integration (HFI)  on the project.

- The suitability of the Allocation of nuclear safety Functions (AoF) between the human and technology.

- The adequacy of HF Engineering (HFE) programme.

- The adequacy of the RP’s approach to the identification, analysis and substantiation of Human Based Safety Claims (HBSCs).

- The adequacy of the HF safety case and design analysis submissions.

- The concept of operations as it currently stands.

# Assessment standards and interfaces

- For ONR, the primary goal of the GDA Step 2 assessment is to reach an independent and informed judgment on the adequacy of a safety, security and safeguards case for the reactor technology being assessed.

- ONR has a range of internal guidance to enable Inspectors to undertake a proportionate and consistent assessment of such cases. This section identifies the standards which have been considered in this assessment.

- This section also identifies the key interfaces with other technical topic areas.

  - Standards

- The ONR Safety Assessment Principles (SAPs) (ref. [6]) constitute the regulatory principles against which the RP’s case is judged. Consequently, the SAPs are the basis for ONR’s assessment and have therefore been used for the Step 2 assessment of the Rolls-Royce SMR.

- The International Atomic Energy Agency (IAEA) safety standards (ref. [13]) and nuclear security series (ref. [14]) are a cornerstone of the global nuclear safety and security regime. They provide a framework of fundamental principles, requirements and guidance. They are applicable, as relevant, throughout the entire lifetime of facilities and activities.

- Furthermore, ONR is a member of the Western European Nuclear Regulators Association (WENRA). WENRA has developed Reference Levels (ref. [15]), which represent good practices for existing nuclear power plants, and Safety Objectives for new reactors (ref. [16]).

- The relevant SAPs, IAEA standards and WENRA reference levels are embodied and expanded on in the TAGs (ref. [7]). The TAGs provide the principal means for assessing the HF aspects in practice.

    - Safety Assessment Principles (SAPs)

- The key SAPs applied within my assessment are EHF.1 to EHF.3, EHF.5 to EHF.7, EHF.10 and EHF.11, MS.2, MS.4, ECS.2, ESS.8 and SC.4.

- A list of the SAPs used in this assessment is recorded in Appendix 1.

    - Technical Assessment Guides (TAGs)

- The following TAGs have been used as part of this assessment:

- NS-TAST-GD-096 - Guidance on Mechanics of Assessment (ref. [5])

- NS-TAST-GD-051 - The Purpose, Scope and Content of Safety Cases (ref. [17])

- NS-TAST-GD-058 - Human Factors Integration (ref. [18])

- NS-TAST-GD-059 - Human Machine Interfaces (ref. [19])

- NS-TAST-GD-062 - Workplaces and Work Environment (ref. [20])

- NS-TAST-GD-063 - Human Reliability Analysis (ref. [21])

- NS-TAST-GD-064 - Allocation of Function Between Human and Engineered Systems (ref. [22])

    - National and international standards and guidance

- The following international standards and guidance have been used to inform my assessment:

- IAEA, Format and Content of the Safety Analysis Report for Nuclear Power Plants, Specific Safety Guide No. SSG-61 (ref. [23]) – chapters:

Chapter 7 - Instrumentation and Control.

Chapter 13 - Conduct of operations

Chapter 18 - Human Factors Engineering

- IAEA, Safety of Nuclear Power Plants: Design. SSR 2/1 (Rev. 1) (ref. [24])

Requirement 32: Design for Optimal Human Performance

- IAEA, Commissioning and Operation of Nuclear Power Plants SSR 2/2 (Rev. 1) (ref. [25])

Requirment 4. Staffing of the operating organisation

- IAEA, Safety Assessment for Facilities and Activities. GSR Part 4 (Rev. 1) (ref. [26])

Requirement 11: Assessment of human factors

- IAEA, Human Factors Engineering in the Design of Nuclear Power Plants, IAEA Safety Standards Series No. SSG‑51(ref. [27])

  - Integration with other assessment topics

- I worked closely with other topics as part of my HF assessment. Similarly, other assessors sought input from my assessment. These interactions are key to the success of GDA to prevent or mitigate any gaps, duplications or inconsistencies in ONR’s assessment.

- The key interactions with other topic areas were:

- Fault Studies to confirm that HBSCs are being suitably and sufficiently captured within the fault schedule.

- Probabilistic Safety Analysis (PSA) to confirm that the approach to HRA and the modelling of HBSCs within the PSA are suitable and sufficient.

- Hazards to confirm that HBSCs are being suitably and sufficiently captured.

- Conventional Health and Safety to minimise any assessment overlap with respect to the design of System Structures and Components (SSCs) and HBSCs substantiation

  - Use of technical support contractors

- During Step 2 I have not engaged Technical Support Contractors (TSCs) to support my assessment of the Topic aspects of the Rolls-Royce SMR.

# Requesting party’s submission

- Rolls-Royce SMR Limited submitted a series of E3S chapters, or summary reports, and other supporting references, which outline the E3S case for the generic Rolls-Royce SMR design. This section presents a summary of the RP’s E3S case for HF. It also identifies the documents submitted by the RP which have formed the basis of my HF assessment of the Rolls-Royce SMR.

  - Summary of the Rolls-Royce SMR design

- The generic Rolls-Royce SMR design is a three loop Pressurised Water Reactor (PWR) with a target electrical power output of 470 MWe (from a thermal power of 1,358 MWth) and a design life of 60 years for non-replaceable components.

- The Rolls-Royce SMR design has been developed by the RP based upon well-established PWR technology, in use all over the world. Innovation comes in the form of its modular approach to construction which would see the majority of the power station built in factory conditions and assembled on site.

- The reactor itself is of a typical PWR design, including a steel Reactor Pressure Vessel (RPV) holding fuel assemblies, Steam Generators (SG), Reactor Coolant Pumps (RCP) and piping, all held within a steel containment vessel. The reactor is equipped with a number of supporting systems for normal operations and a range of safety measures are present in the design to provide cooling, control criticality and contain radioactivity under fault conditions. Passive safety features are preferred to active components, reflecting the RP’s design philosophy.

- The Rolls-Royce SMR design presents several novel features that I have considered relevant to my HF assessment. These comprise:

- The compact layout which requires careful consideration of human and equipment access / egress.

- Deployment of internal supporting modular structures for safety systems and components which could lead to contested internal space allocations if not suitably managed.

- Implementation of aseismic bearings to absorb seismic energy. EMIT and replacement of these through-life may introduce new operator tasks carried out within a confined space.

  - E3S case approach and structure

- Rolls-Royce SMR Limited has chosen to develop its cases in a holistic manner, as an Environment, Safety, Security and Safeguards (E3S) case. The overall objective for the E3S case is to demonstrate that the design will ‘protect people and the environment from harm’.

- This means that, although the case made for each of the E3S purposes (i.e. environment, safety, security and safeguards) will inevitably be different at the top level, it will draw upon common evidence outputs (as well as other non-common outputs) to substantiate each of the purposes. This is claimed to offer benefits in terms of clarity, integration and understanding impacts from any changes to the case.

- The E3S case is being developed using a three-tier hierarchy and incorporating a Claim, Argument and Evidence (CAE) structure with the highest-level claims being derived from the RP’s own E3S principles. The highest level of the three tiers is the RP’s Tier 1 E3S chapters, with the lower tiers providing more detailed arguments and evidence. This is illustrated in Figure 1.

Figure 1: Claim, Argument and Evidence (CAE) structure within the E3S hierarchy (ref. [1])

- The structure of the E3S case largely aligns with the IAEA guidance for safety cases, SSG-61 (ref. [23]), supplemented to include UK specific expectations and expanded to include the other E3S purposes.

  - Summary of the requesting party’s E3S case for HF

- The treatment of HF and human contribution to risk is summarised within Chapter 18 of the E3S case (ref. [3]). The chapter outlines the RP’s claims, arguments and evidence underpinning its design. The fundamental HF claim, is:

- The integration of Human Factors into the design minimises risks to humans to As Low As Reasonably Practicable (ALARP).

- Human based actions enable safe and secure operation and maintenance of the Rolls-Royce SMR throughout the lifecycle of operation and all operating modes.

- The Rolls-Royce SMR design is informed by assumptions on the capability of a future licensee from a Human Factors perspective.

- The treatment of the human factors aspects of the Best Available Technique (BAT), Tasks important for Nuclear Security (TINS) Secure by Design, and Safeguards by Design is currently not developed to a stage where any differences in HF approach can be articulated within the E3S case. The current informal claim is simply that the RP’s HF team are proportionally supporting in these areas on a needs basis. Further detail is anticipated at Step 3.

    - Human Factors Integration

- The RP’s route map (ref. [28]) states the following sub claim for the integration of HF into the design and E3S programmes:

- L 1 Human Factors is integrated into the design based on sound safety principles and methods that minimise risks to ALARP.

L 2 A suite of Human Factors activities are carried out to integrate HF into the Rolls-Royce SMR design.

L 2 Human Factors requirements are derived from principles, standards, RGP and OPEX.

Figure 1 below (ref. [29]) summarises the RP’s approach for HFI.

Figure 2 – HFI approach (ref. [29])

    - Human Reliability Assessment

- L1 “Human based actions enable safe and secure operation and maintenance of the Rolls-Royce SMR throughout the lifecycle of operation and all operating modes.”

L 2 “The operator actions required to operate and maintain the Rolls-Royce SMR are identified.”

L 2 “The operator actions required to operate and maintain the Rolls-Royce SMR are substantiated.”

    - Human Factors Engineering

- The underpinning level 1 sub-claims are presented within the RP’s safety case route map (ref. [28]). The route map states the following sub claim for the integration of HF into the design and E3S programmes:

- L1 “The Rolls-Royce SMR design provides the operators with the facilities to enable safe and secure operation and reduces risks to As Low As Reasonably Practicable throughout the lifecycle of operation and all operating modes.”

L2 “The Rolls-Royce SMR design accommodates the target population.”

L2 “The Rolls-Royce SMR equipment and layout supports the reliable performance of the operators through-life.”

- L 1 “The Rolls-Royce SMR design is informed by assumptions on the capability of a future licensee from a Human Factors perspective.

L 2 “The Rolls-Royce SMR can be safely operated and maintained through-life by a future licensee’s organisation.”

    - ALARP

- ALARP is recognised within the RP’s primary claim for HF: “The integration of Human Factors into the design minimises risks to humans to As Low As Reasonably Practicable (ALARP)” (ref. [3]).

- Within the hierarchy of claims, the RP notes that this will be achieved via the adherence to relevant good practice and where this is not possible, the adoption of computational approaches that balance the pros and cons of options.

  - Basis of assessment: requesting party’s documentation

- The principal documents that have formed the basis of my HF assessment of the E3S case are:

- Human Factors Integration Plan for the RR Small Modular Reactor 	 (ref. [29]). This report sets out the RP’s approach for managing HF during the GDA.

- Rolls-Royce SMR HMI Style Guide (ref. [30]). This sets out the HFE design guidance for the project. It is used in concert with a requirements database that applies to all systems, structures and components.

- Rolls-Royce SMR Target Audience Description (ref. [31]). This document characterises the end use of the Rolls-Royce SMR design.

- Rolls-Royce SMR Human Reliability Analysis: Quantitative Assessment Strategy (ref. [32]). This document sets out the RP’s approach to quantitative HRA.

- Rolls-Royce SMR Human Reliability Analysis Strategy (ref. [33]). This document sets out the RP’s approach to qualitative HRA.

- Rolls-Royce SMR Concept of Operations (ref. [34]). This document sets out the role of the operator on the Rolls-Royce SMR.

- Rolls-Royce SMR Human Factors Programme (ref. [35]).

- Rolls-Royce SMR Allocation of Function Summary Report (ref. [36]). This document sets out the RP’s approach to Allocation of Function (AoF) and summarises the work done to date in this area.

- Rolls-Royce SMR Rolls-Royce SMR Control Facilities Description (ref. [37]). This document describes those control facilities considered within scope of GDA. It also summarises the work done to date.

- Rolls-Royce SMR Human Reliability Analysis Progress Report (ref. [38]). This report and reference [39] summarise the HRA work done to date.

- Rolls-Royce SMR Human Factors Risk Summary (ref. [39]). This report summarises the human contribution to risk based on the latest PSA / DSA (Deterministic Safety Analysis) information.

- Rolls-Royce SMR Task Analysis Summary (ref. [40]). This report summarises the task analysis work done to date.

- Rolls-Royce SMR Human Factors Engineering Summary (ref. [41]). This report summarises the HFE work done to date.

- These documents internally reference other domains, such as Environmental and Security, but any differences in approach have not been articulated within the E3S case. The current informal claim is simply that the RP’s HF team are proportionally supporting in these areas on a need’s basis.

# ONR assessment

  - Assessment strategy

- To fulfil the aims for the Step 2 assessment of the Rolls-Royce SMR, my assessment strategy (ref. [10])  targets the following matters proportionately. The scope of my assessment comprises.

Assess the ongoing suitability of the HFI programme to support the progression of a meaningful GDA during Step 2.

The capability and capacity of the Rolls-Royce SMR HF team to deliver the scope of HF Integration.

The approach to Operational Experience (OPEX) and Learning From Experience (LFE) for design, safety analysis, build, commissioning, operation and decommissioning to ensure that appropriate learning is being taken account of.

The suitable and sufficient integration of HF across the safety analysis scope to ensure that the human contribution to risk is understood, and in demonstrating that it is reduced ALARP.

The suitability and sufficiency of the HF safety analysis methods being applied to ensure that they meet relevant good practice and thus support the demonstration that risks are reduced ALARP.  I focused on the following areas as they contribute the greatest risk to successfully completing a meaningful GDA:

The effectiveness of the process for identifying, categorising, and classifying, HBSCs.  Without an effective identification process, it is impossible to meet the legal duty of a suitable and sufficient risk assessment.

The suitability of any substantiation of HBSCs by task and error analysis.

Aspects within the HF safety analysis methods where there is limited relevant good practice, or uncertainties arising from that.  Where such uncertainties are identified, for example, in the area of HRA in relation to screen-based control rooms, I will seek assurance that suitable conservatism is being applied to account for these uncertainties.

Where available in Step 2, a proportionate sample of substantiation evidence in areas such as: Hazards, Severe Accident Analysis (SAA), etc. to gain confidence that the human contribution to risk is being appropriately recognised across the E3S case.

The AoF process. AoF determines the optimum balance of Human and Technology delivered functions across operations, safety, security and safeguards. Effective AoF is fundamental to ensuring a safe and operable design as it ensures human and technological components of the wider socio-technical system are matched to their relative strengths, whilst mitigating their weaknesses. It also informs decisions in relation to hierarchy of control.

Assessment of the concept of operations submission for the Rolls-Royce SMR. In conjunction with the AoF analysis, this provides confidence that the fundamental basics of the design are optimised and can support a safe and secure deployment within GB.

The modular concept and compact layout presents smaller internal volumes in comparison to larger reactor designs. The potential for any detrimental effects to HBSCs will be investigated to ensure that sufficient space is allocated to support claimed human actions. For Step 2, this will focus on the process used to ensure that space is protected. Step 3 will focus on confirming that the process was successful.

The general design process to gain confidence that HF is being suitably integrated into safety, security, and safeguards to ensure that risks are reduced ALARP and that the design is safe, secure and operable.

The adequacy (in relation to modern standards) of the declared suite of HF-related design standards being used to influence the design.

The adequacy of the any standards-in-design approaches to ensure that suitable HF oversight is being maintained, i.e. where non-HF SQEPs are following HF design standards to integrate HF.

The RP’s approach to design and task Verification and Validation (&V). Effective HF V&V is key to demonstrating that human actions are risk reduced ALARP. Outputs of this process will be sampled if they are available during Step 2.

The RP’s approach to integrating HF principles into the future decommissioning activities.

  - Assessment

    - Human Factors Integration

- This section presents my assessment of the enabling factors necessary to deliver an integrated programme of HF work in support of the development of the RP’s design and E3S analysis.

- ONR’s SAP EHF.1 sets the expectation that there should be a systematic approach to integrating HF within the design, assessment and management of systems and processes applied throughout the facility’s lifecycle. Similar expectations are established in IAEA requirements, i.e., requirement 32: design for optimal operator performance (ref. [24])

- Fundamental to the effective and proportionate consideration of the limitations and capabilities of the human within the design, is a HFI programme. It ensures that HF is properly considered, and hence contributes to the principle of ALARP. Throughout my assessment, I place significant reliance on the efficacy of the HFI process as it gives confidence that HF is being appropriately considered throughout the design.

- ONR’s expectations for the integration of HF in nuclear safety are set out within NS-TAST-GD-058 (Rev 4) Human Factors Integration’ (ref. [7]). I recognise that there are other formal requirements for the consideration of HF in other areas such as Environment, Security and Safeguards, but these are not considered in detail within this assessment report as they covered by other regulators and ONR disciplines where appropriate. I have, however, attempted to confirm consideration of these areas within the RP’s wider HFI programme.

- The HFI expectations can be summarised as the RP (or licensee) demonstrating suitable and sufficient processes and arrangements in the following areas (The bracketed numbers indicate which section of this report they are assessed in):

- The capability and capacity of the organisation / HF team (4.2.1)

- The scope of HFI (4.2.1)

- Technical programme (4.2.1)

- Managing issues and assumptions (4.2.1)

- Operational experience (4.2.1)

- Standards, codes, and methods (4.2.1)

- Target Audience Description (TAD) (4.2.1)

- Concept of operations (4.2.2)

- The RP’s objectives (ref. [29]) for the Rolls-Royce SMR design broadly align with the above expectations in that they aim:

- To support the design, in a fully integrated manner, through provision of HF policies, requirements, guidance and support.

- To ensure that HF support to the project is managed and integrated in a way that ensures a consistent approach across the scope of the project, and throughout its duration.

- To ensure that HF issues are considered in the design solution, and to provide appropriate analysis and evidence to support design decisions.

- To ensure that system designs are optimised from a HF perspective, as far as is practicable, to deliver a safe, efficient and effective set of human-system interactions in the design solution.

#### Assessment of the RP’s human factors organisational capability and capacity

- ONR’s SAPs, EHF.8 and EHF. 11 set the expectation that there will be sufficient SQEP HF resource delivering the relevant HFE and safety analysis work. SAP MS.2 also sets the expectation that organisations should have the capability to secure and maintain the safety of their undertakings.

- The efficacy of the HF capability within an RP organisation is predicated on several enabling factors. These include:

- Sufficient agency to effect necessary design modifications to ensure that human error is reduced ALARP.

- Proportionate and targeted integration that minimises both future human errors on site and the design-foreclosure risk from a lack of timely HFI.

- Sufficient personnel to support the HFE and E3S analysis programmes.

- Suitably SQEP individuals.

- The HF lead role includes responsibility for HF, Operations, and Integrated Logistical Support and Maintenance. This role sits two layers down below that of the Project Chief Engineer, which I consider provides a suitable degree of agency to effect change. The ‘HF Lead’ role itself does not have responsibility for HF, Operations and Integrated Logistical Support and Maintenance. These are the responsibility of the ‘HF and Operations Integration Manager’ role. Currently, the same person holds these two roles, however the organisation is structured to allow these roles to be held by separate persons as the team sizes and work demands increase.

- One benefit of integrating HF and maintainability is that it can improve the consideration of HF principles within EMIT activities. This is important on highly automated and passive reactors as they are typically (in relative balance of risk terms) more sensitive to EMIT (Type A) errors than operator errors during fault responses due to the contribution to safety of the automation and passive safety features.

- Further, the RP has adopted a systems-based engineering approach for the development of the Rolls-Royce SMR. Underpinning this process is a system called Dynamic Object Oriented Requirements System (DOORS). This database manages all of the E3S requirements, such that an engineer working on a specific SSC will be provided with a comprehensive set of design requirements (including HF) that they must comply with. HF requirements are tied to an associated verification plan, which sets out what evidence of compliance is required. Depending on the risk-importance, or technical complexity of the requirement, these can be completed by: The designer; A HF engineer and the designer in concert; or solely by the HF team.

- Compliance with the HF requirements are supported by HF checklists (83 created during Step 2 (ref. [41]) which will be developed for every design team – the adequacy of the checklists is discussed later in section 4.2.2. but are generally fit for purpose with some degree of improvement required. The RP recognises this and they are subject to ongoing development.

- As part of the system-engineering approach, gated reviews are used to periodically confirm that the design meets its stated requirements. For the Definition Review (DR) process, HF is a mandated stakeholder.

- In addition to the DOORs based requirements integration, the HF team are also providing support on a needs basis for activities like HAZOPs, HAZIDs, design reviews, HRA, etc.

- Given the small size of the RP’s HF team I consider this to be a proportionate and good practice approach at this stage to maximise the reach of the HFI programme and reduce the risk from human error ALARP.  Based on timeliness of delivery and quality, I consider the HF capability capacity has been sufficient for Steps 1 and 2 of this GDA. It is also positive to note that the RP recognises the future risks around capacity and is currently planning the future programme of work to manage this risk.

- As this approach is evolving, it has some implementation challenges, I will monitor capability and capacity during Step 3 as a residual matter.

#### Assessment of the scope and planning of HFI

- ONR’s SAP, EHF.1 sets the expectation that there will be a systematic approach to integrating human factors within the design, assessment and management of systems and processes and that this should be applied throughout the facility’s lifecycle.

- With respect to the declared scope of HFI, I consider the RP to have followed best practice in this area. HF is claimed within Chapter 18 of the PCSR (ref. [3]) to be integrated across the full E3S case, which moves beyond the traditional focus on just safety.

- HF principles and RGP is also being integrated within the Conventional Health and Safety (CH&S), Construction Design and Manufacture (CDM), Security, Safeguards, and Environmental scopes of work (ref. [41]). It also includes all phases of the product lifecycle.

- Whilst I commend the RP for establishing such an ambitious scope of HFI, there has been a focus on nuclear safety to date, with only limited HF work being carried out the areas of Environment, CH&S, Security and Safeguards domains (ref. [41]).

- The RP’s HF team have, at this time, supported one Vital Area Assessment (VAI).

- For CH&S, no evidence has been submitted, but the RP has claimed that this is work in progress and that the HF team have been upskilled via Institute of Occupational Safety and Health (IOSH) training.

- No evidence of HF support to the Environmental case was provided.

- No evidence of HF support to the Safeguards case was provided.

- For Step 2, I am content with this degree of integration with safety given the design maturity and the clear statement of intent. However, for Step 3, ONR and the EA will need to monitor HF integration into the wider E3S case to ensure that the RP delivers against its statement of intent.

- The RP provided an initial HFI programme (ref. [35]) to provide an overview of activities and timescales, finishing end of 2024. Whilst this was useful during Step 2 for me to gain confidence that the RP had both an understanding of HFI scope and how long activities may take, the detail within was too high-level to be an effective HFI tool as it was missing the following detail:

- No human resource loading to demonstrate that the programme was deliverable with the current resource.

- No indication of inter and intra HF dependencies, which would demonstrate that design foreclosure risks were understood and could be managed.

- No critical-path showing how long the programme will take to deliver.

- Whilst sufficient for Step 2, I consider that adopting a similar approach for Step 3 would not adequately support effective HFI across the SMR programme. A further consideration is that the lack of detail also creates risk for ONR’s GDA programme with respect to ensuring sufficient resource is available when necessary to assess submissions.

- These expectations have been communicated to the RP (ref. [42]).

- To conclude, I am content that the RP’s HFI scope meets relevant good practice for nuclear safety. It is also positive that the RP recognises the importance of HF across the other functions that exist on a nuclear power plant, namely, Environmental, Safeguards, and Security. However, the RP has yet to define in detail what this scope of HF work will look like and therefore this should be assessed by the relevant discipline within Step 3 as residual matters.

#### Assessment of the RP’s approach to managing issues and assumptions

- ONR expects (ref. [18]) that duty holders develop a suitable and sufficient arrangements for managing:

- HF issues identified during design and analysis work.

- Assumptions made during the progression of the design and analysis for future validation, either within the design authority or by the customer / duty-holder.

- The RP’s system for managing issues and assumptions is Risks, Assumptions, Issues, Dependencies and Opportunities (RAIDO) (ref. [29]). This system is owned by the RP’s HF team but can be populated by either team members or project personnel. For step 2, there is submitted evidence (ref. [29]). that it is being used, but the content is limited due to its recent introduction and lack of detailed HF design and analysis work.

- I therefore chose not to sample RAIDO content in Step 2, but consider the basic features of the system meet RGP as there is a credible process for populating the database and it clearly captures both issues and assumptions. I also note positively that it has extended the remit of a typical issues and assumptions register by the inclusion of Dependencies and Opportunities.

- I will sample RAIDO content during Step 3 as residual matters to confirm that the RP is adequately identifying, categorising, sentencing RAIDOs, along with adequately implementing solutions where appropriate.

#### Operational experience and learning from experience

- ONR expects (SAP MS.4 Learning) that lessons should be learned from internal and external sources to continually improve leadership, organisational capability, the management system, safety decision making and safety performance. The expectation that new designs implement learning from pre-cursor or similar designs is also enshrined with various IAEA guides (refs. [23] and [25]).

- My expectation is that this learning would be translated into design and future operational requirements and guidance.

- In this area, my assessment found some shortfalls against expectations. Whilst the RP has started work in this area, it is limited in nature, and focussed on deriving Postulated Initiating Events (ref. [41]) for Step 2. The RP does formally recognise (ref. [41]) this, however, and has a clear statement of intent that additional OPEX reviews will be undertaken. I am also aware that the HF team has been liaising with its operational partners to identify learning that can be included within the Rolls-Royce SMR design. I have yet to see the output of this work though.

- Whilst this is a shortfall in regulatory expectations, it is mitigated by the design maturity and ongoing work in this area with the RP’s operational partners, such that there is sufficient time for the OPEX reviews to become more comprehensive and any learning incorporated into the design.

- I will follow up the topic of OPEX during Step 3 as residual matters.

#### Assessment of methods, standards and guidance.

Allocation of Function

- ONR expects (EHF. 2 ref. [6]) that: “When designing systems, dependence on human action to maintain and recover a stable, safe state should be minimised. The allocation of safety actions between humans and engineered structures, systems or components should be substantiated.”  Allocation of Function (AoF) is also a clear expectation within IAEA guidance (ref. [23])

- AoF is a fundamental process within complex systems design and is done by systematically considering identified capabilities and limitations of humans and technology and their relative failure likelihoods separately or jointly in delivering a function. This is done with the aim of producing an optimal design solution for function delivery and thereby minimising failure risk to ALARP.

- Traditionally, AoF has applied only to nuclear safety functions, but current RGP, and thus ONR’s expectations (ref. [22]), extend AoF to all functions. This is due to their interrelated and sometimes conflicting nature. An additional expectation is that whatever AoF methods are selected, they recognise that automation capability far exceeds what was previously possible on previous generation designs.

- Thus, I would expect the RP to consider the following functions as a minimum:

- Operational

- Safety

- Safeguards

- Security – both Protective Security and Cyber

- Environmental

- I would also expect that AoF determinations go beyond binary solutions and consider the human implications of too much automation, and the impact of automation failure on operating personnel. Thus, I expect decisions to balance the implications of automation failure as well as the expected benefits.

- The RP’s submission discusses its method and work to date in its “Allocation of Function Summary” (ref. [36]). I note that it cites ONR’s recognised RGP in this area: BS EN 61839:2014: Nuclear power plants – Design of control rooms – Functional analysis and assignment (ref. [43]) as a key input into its methodology. It claims to also be informed by similar NUREG and EPRI methodologies.

- The resultant method is summarised (ref. [43]) below, in Figure 3

Figure 3: Allocation of Function method (ref. [44])

- I consider this approach generally aligns with regulatory expectations in that it is clearly based on international RGP. The method specifically recognises:

- Higher degrees of automation are not necessarily a panacea for system reliability.

- That job satisfaction and situational awareness are both important factors when determining human-in-the-loop levels.

- The impact that automation failure can have on the human with respect to system reliability.

- That automation design has moved beyond person vs machine (e.g. it recognises the various work on Levels of Automation (LOA)).

- Any automation assumptions are being captured in RAIDO for future analysis and validation.

- However, there are some shortfalls against RGP in the current methodological approach; albeit non-prejudicial to a successful GDA at this stage, as I consider there is plenty of opportunity to address them.

- The AoF method does not adequately consider the inter-related nature of the wider E3S functions. There is little to no reference to Environmental Safety and Safeguards within the method, and Security will be looked at in the future. The RP states (ref. [36]) that this is due to design maturity limitations, but impact of security requirements on safety functions should be considered during the allocation of safety functions, which are being cosidered now, to minise re-design and de-risk design foreclosure.

- I will sample the application of the AoF method and its outputs in much greater detail during Step 3.

- The output from the AoF method is considered within Section 4.2.3 below.

Target Audience Description

- ONR expects (NS-TAST-GD-058 ref. [7]) that, for new-build projects, the physical, mental, cognitive, eductational, and cultural characteristics of the indended user population are captured and used to inform the design.

- The RP has produced a TAD (ref. [31]) describing the characterstics of its assumed user population. It considers:

- The full range of worker populations (based on UK data), from the manufacturing side to operations (including security), through to decommissioning.

- The anthropometric range of human sizes (1-99 percentile), including consideration of secular changes in size and PPE accommodations. It also recognises the requirements for inclusivity in design.

- Physiological factors.

- Cognitive and Educational characteristics and limitations.

- Cultural characteristics.

- It also recognises that future work is required to better inform: EMIT space allocation, consideration for evacuation, and to provide references for the appropriate human CAD models for the engineering teams to use to ensure the user is considered as part of the plant layout.

- I consider the TAD to be generally fit for purpose at this stage, and cosider its scope meets RGP. However, there are some minor shortfalls in the current iteration relating to obvious missing physiological and cognitive characteristics, and a lack of clarity in its relationship between it and other guidance material (the Style Guide ref. [30]) . Having multiple documents with overlapping and complementary material could impact the utility of the guidance with non expert users. I note the intention of requirements to be managed via the DOORS database so this may not actually be a problem in practice.

- The RP is cogniscant of the minor improvements needed and have committed to update it during Step 3.

- Given this document will be updated, I will revisit it, and its application, during Step 3 to ensure that it is demonstrably influencing the design.

Assessment of style guide / Human Machine Interface guidance

- ONR expects (ref. [6] and [19]) that suitable and sufficient user interfaces should be provided at appropriate locations to provide effective monitoring and control of the facility in normal operations, faults and accident conditions. ONR also considers plant equipment such as valves, emergency supply connection points and similar plant and equipment to be user interfaces.

ONR also expects (ref. [19]) that the working environment be optimised to minimise human error.

- Thus, there is an expectation that an RP will establish suitable and sufficient requirements and guidance to deliver against these expectations. The RP does this in several ways:

- The Rolls-Royce SMR HMI Style Guide (ref. [30]), which summarises and captures the identified project relevant design guidance and requirements, and is the key focus of this section.

- The DOORs database, discussed above.

- Human Factors checklists (sample ref. [44]), discussed in this section.

- My assessment of the HMI style-guide (ref. [30]) found multiple minor shortfalls against expectations indicative of a document that is work-in-progress. This is explicable by the fact that the guide was written early in the project and is considered by the RP to be a ‘live’ document which will be subject to regular updates.

- These shortfalls included:

- Lacking in expected scope and detail as it does not cover / has insufficient coverage of:

Tool design.

Communications design.

Lighting design.

Guidance on delivering human-centred automation.

Safety classification and how the guide should be applied proportionally.

Basic HF layout principles, such as: frequency of use, importance, and co-location.

Error prevention principles in design.

Modularisation.

- Lack of substantiation of why standards are considered to be appropriate.

- Obvious RGP standards not identified, e.g. EEMUA 191 (ref. [45]) on alarm design.

- Missing legislative requirements, e.g., Lifting Operations and Lifting Equipment Regulations 1998 (LOLER) (ref. [46]) and Provision and Use of Work Equipment Regulations 1998 (PUWER) (ref. [47]).

- These shortfalls were fed back to the RP early in Step 2 (ref. [48]) to which it responded positively and indicated that they would be addressed in future updates. Therefore, whilst the shortfalls are manifold, they are minor in nature, and their lack of inclusion is largely mitigated by their questionable utility at this concept design stage as they are typically of more use during detailed design.

- I am content for the RP to address them in future updates and will monitor progress accordingly during Step 3 to ensure that guidance is developed at an appropriate pace to ensure the design meets HF RGP expectations.

- Because of the shortfalls in the Style Guide (ref. [30]) I chose to only sample a single design checklist to determine how the requirements were being represented within said checklists. Unsurprisingly, I found similar scope shortfalls, which are discussed further in section 4.2.3 where I discuss their application.

- A more comprehensive and targeted sample will be carried out during Step 3 to provide assurance that the checklists are driving suitable and sufficient HFI across the design.

- Like the style guide, I am not overly concerned over the maturity I found at Step 2, as this is a reflection of the general design maturity across the project. I am confident that the RP has the technical capability to evolve the checklists to a level that will ensure suitable and sufficient HFI within the design.

Use of Computer Aided Design

- ONR expects (ref. [6], [19]) [19]) that the working environment be optimised to minimise human error. Therefore, suitable design and validation approaches need to be employed to ensure that humans can operate reliably within the plant environment. This is typically done via the adherence to codes and standards and by modelling the human within the physical environment either via CAD or via physical mock-ups.

- It is positive to note that the RP recognises the HF contested space challenges that potentially exist with SMR design, as whilst reactors can be scaled, human operators cannot, so EMIT and access / egress risks may increase for SMR designs.

- The RP has introduced sophisticated human CAD and virtual reality software to support the design process that allows the modelling of human interactions with the evolving virtual design. This has significant potential benefits when it comes to validating space envelopes around SSCs to mitigate design foreclosure risks around EMIT, access / egress and potential evacuation. I welcome the pro-active approach adopted by the RP here as the smaller footprint of SMR designs pose potentially significant HFE challenges to the designer attempting to accommodate human operators.

- Whilst I have observed a demonstration of this capability, I have not formally assessed its application during Step 2, as it was too early to do so using real examples.  I will assess its application during Step 3 to confirm that it is being used to actively de-risk contested space within the Rolls-Royce SMR design.

Assessment of the approach to HBSC identification, task analysis and substantiation methods

HBSC identification approach

- ONR expects (SAP EHF.3 ref. [6] and (ref. [21]) that a systematic approach should be taken to identify human actions that can impact safety for all permitted operating modes and all fault and accident conditions identified in the safety case, including severe accidents.

- The analysis should be conducted as part of design basis analysis, probabilistic safety analysis and severe accident analysis aspects of the safety case (see Fault analysis, paragraph 605 ff.). Proportionate analysis should be undertaken to support the claims and arguments made in regard to these actions and administrative controls. (SAP EHF.10 ref. [6]).

- The scope of HRA should include: pre-fault human actions during maintenance, calibration or testing activities where error could result in the non-availability of equipment or systems important to safety (Type A), actions that contribute to initiating events (Type B), post-fault human actions; and long-term recovery actions in severe accidents (Type C) (SAP EHF.10 ref. [6]).  Contingent operator actions and dependent human errors committed by single or multiple operators should be modelled explicitly in the human reliability analysis and accounted for quantitatively. The analysis should also account for indirect dependence and avoid unrealistically low single or combined human error probabilities being propagated through the fault analysis. (SAP EHF.10 ref. [6]).

- The RP’s approach to qualitative and quantitative substantiation of HBSCs can be found in the following reports:

- “Rolls-Royce SMR Human Reliability Analysis Strategy” (ref. [33]), which covers the overall process and detailed qualitative assessment requirements.

- “Rolls-Royce SMR Human Reliability Analysis: Quantitative Assessment Strategy” (ref. [32]), which describes the RP’s approach for numerical assessment of human reliability.

- Figure 4 (ref. [33]) summarises the RP’s general approach to the E3S analysis and how HF fits into this process.

Figure 4 HRA and E3S Case Terms and Relationship (ref. [33])

- With respect to safety, the RP’s general approach aligns with regulatory expectations for nuclear safety in that HF is being integrated into the initial hazard analysis and derivation of Postulated Initiating Events (PIEs) (ref. [41]).

- Security is not adequately covered within the strategy, although the RP has identified a future need for it to do so. Further, the treatment of risk important human actions supporting the Safeguards, Conventional, and Environmental cases is also not discussed. Again, the RP notes this omission within this document, but it is clearly within E3S scope (ref. [3]).

- Whilst the qualitative HRA approaches between these domains are unlikely to differ significantly between each other in terms of evidence gathered and Hierarchical Task Analysis (HTA) methods, there are differences, for example, substantiation of Tasks Important to Nuclear Security (TINS) is done via a 3-Level system. Given this is a strategy document, setting out the project approach, I would have expected specific references to be made along with any differences in application and this is not the case. I will follow this up as a residual matter during Step 3.

- ONR and the EA will seek assurance during Step 3, that HF is adequately supporting all the E3S functions and not just nuclear safety.

- I have not sampled any of the Hazard Identfication (HAZID) minutes during Step 2 so cannot comment on specific HF contributions but will during Step 3.

Task analysis approach

- This section assesses the RP’s methods for task substantiation. For Step 2 I have focussed my assessment to the RP’s approach to Tabular Task and Error Analysis (TTA) as they are not carrying out HF Verification and Validation activities until later in the GDA. I will consider these approaches during Step 3.

- ONR expects that, following the identification of HBSCs, proportionate analysis should be carried out of all tasks important to safety and used to justify the effective delivery of the safety functions to which they contribute (SAP EHF.5 ref. [6]).

- The RP’s approach (ref. [40]) to TTA captures the following data.

- Unique identification #

- Plan indicating the task sequencing

- Task description

- Task step time

- Cumulative time

- Personnel details

- Supervision requirements

- Location

- Controls

- Indication details / requirement to support the task

- Interface details / requirements to support the task

- Tools and equipment

- Action type

- Human error identification

- Consequences of error

- Mitigation or recovery details

- Additional supplementary information

- Recommendations and requirements resulting from the application of this approach are tracked via the RAIDO system.

- This approach to task analysis generally aligns with RGP (ref. [21]) and is sufficient to support Step 2 to support the development of the design. I specifically note that the RP has included opportunities for recovery in its analysis as this often identifies new risk important actions that may not have been discovered within Postulated Initiating Event (PIE) and HAZOP / HAZID analysis and the derivation of the fault schedule.

- However, I identified some minor omissions that will need to be considered during Step 3 once the task analysis moves from informing the design, into substantiating what has been designed, e.g. it is part of a suitable and sufficient risk assessment.  For example, current omissions include.

- Job and organisational factors, such as training and procedural requirements

- Communications requirements

- Environmental factors

- Situational awareness

- Cognitive workload

- Violation potential

- I will follow this up as a residual matter during Step 3.

- The RP did not submit any TTAs for assessment during Step 2, so I can only conclude at this stage that the general approach is fit for purpose, assuming that, as the design matures, the assumptions being made are replaced by substantiative evidence as part of the TTA programme.

Human Reliability Analysis approach

- This section assesses the RP’s methods for HRA. The RP has not submitted any detailed HRA for assessment within Step 2, so this aspect is out of scope for this step. The application of the declared HRA methods will be a key area of assessment for Step 3.

- ONR expects that Human reliability analysis should identify and analyse all human actions and administrative controls that are necessary for safety SAP EHF.10 (ref. [6]). SAP FA.13 (ref. [6]) requires that the PSA include contributions to risk from pre-fault human errors (type A), human errors leading to faults (type B) and post-fault human errors (type C).

- The RP’s declared (ref. [32]) approaches to HRA comprise the following six methods:

- Application of initial screening data of 1.00 × 10-02  for each HBSC modelled in the PSA.

- Use of industry OPEX, e.g. NUREG/CR-5750 - Rates of Initiating Events at U.S. Nuclear Power Plants: 1987 - 1995 (ref. [49]).

- Technique for Human Error Rate Prediction (THERP) (ref. [50]).

- Human Error Analysis Reliability Technique (HEART) (ref. [51]).

- Standardised Plant Analysis Risk – HRA (SPAR-H) (ref. [52]).

- Absolute Probability Judgement (APJ).

- I consider the use of screening data as a proxy for best estimate analysis appropriate at this stage, as the benefits of a functional PSA are significant with respect to targeting design and analysis effort. I also consider Human Error Probabilities (HEPs) of 1.00 × 10-2 should be easily achievable on a modern plant that has been subject to a suitable and sufficient HFI programme.  However, this may not be suitably conservative for areas of substandard design. I therefore asked via RQ1151 (ref. [53]) the RP to carry out sensitivity analysis on the HRA using more conservative data. I discuss the output of this sensitivity analysis in section 4.2.2, but what is relevant to this section is that the RP were able to demonstrate competency in the use of PSA importance measures for HRA.

- Similarly to the use of screening data, I consider the use of OPEX for postulated initiating events is appropriate for the early development of the PSA. However, it does not replace the need for a suitable and sufficient risk assessment due to the contextual differences between 1960s and 70s era US NPPs and the Rolls-Royce SMR design. I will seek confirmation during Step 3 that the data used is subject to an appropriate validation programme to ensure that is both, best estimate, and underpinned by suitable HF analysis.

- The methods THERP, HEART, SPAR-H proposed for the HRA are well established and have been applied on previous GDAs, so I am content for them to be used on this GDA, with the following caveat. None of these methods are validated for modelling screen-based interactions, and prior ONR research in support of previous GDAs, has shown that they have the potential to produced optimistic HEP data. On this basis, given that no validated tools exist, the RP will need to ensure that a degree of conservatism is applied where human-computer interactions are being modelled. I will monitor the RP’s approach to modelling screen-based interactions during Step 3 to confirm it suitably mitigates the impact of using (without alternative options) non-validated HRA tools.

- With respect to Absolute Probability Judgement (APJ), I do not consider this represents good practice as it is essentially structured ‘estimating based on personal experience and humans are notoriously unreliable at predicting their own performance. Its use should be considered very carefully given its limitations, with a focus on robust underpinning qualitative assessment.

- Other minor issues identified during assessment, which the RP has committed to address in future updates, include.

- The strategy (ref. [33]) does not clearly articulate how the wider HRA will be used to target and prioritise HFE.

- The approach to sensitivity analysis, and how this will be used in not clearly articulated e.g. use of risk achievement worth, risk reduction worth, Fussell-Vesely values (although they have demonstrated competence in this area).

- Differences between HRA supporting DSA and PSA are not clearly explained.

- There is no approach presented for the assessment of violations.

- Whilst further development of the approach to HRA is needed to fully meet regulatory expectations, I consider the RP has established a sound baseline approach as it applies well established methodologies and includes an ambitious scope of assessment that meets best practice. The RP also recognises the shortfalls identified to date and has committed to addressing them in future updates.

#### Conclusion

- For Step 2, because of the lack of design maturity, I have focussed my assessment on confirming that the RP has established an effective HFI programme, established a suite of HF methods and standards and guidance that align with RGP, and created a suitable organisation to support its delivery.

- I consider that the RP has established a small but capable HF organisation. This organisation has developed an ambitious HFI programme of work and delivered – based on my assessment – generally high-quality work to date. The RP is commended for recognising that HF is not just relevant to nuclear safety, but also to all aspects of the operation of a Nuclear Power Plant. However, I note the size of the HF organisation and the risk this presents to future delivery. This is not prejudicial to entry into Step 3, but it may be a risk to the successful completion of the GDA.

- I consider the HF RGP selected for the Rolls-Royce SMR design broadly meets regulatory expectations but note that further work is required in this area as it is currently incomplete. I will follow this up during Step 3 to ensure that the RGP selected supports the demonstration of As Low As Reasonably Practicable (ALARP) (as far as is practicable within GDA).

- The RP has established a suitable approach to determine an optimised balance between engineered systems and human delivery of functions – noting that evidence of application to Environment, Security and Safeguards was not submitted in Step 2. I will monitor the inclusion of the full scope of the E3S in the AoF process during Step 3. I will also sample, a range of AoF decisions to ensure that they have adequately followed the RP’s declared process, and any subsequent HFE work supporting the implementation of the function.

- The RP has also established a generally suitable approach for the identification of HBSCs. Further, there is evidence that these are being captured in both the PSA and the Fault Schedule.

- I consider that the RP has made an effective start in developing a suite of methods and guidance that should support an effective HFI programme. It has also sought to leverage modern design tools which will help mitigate the lack of HF resource currently available within the RP (for example, the use of requirements management tools and human CAD systems). It is positive, that where minor shortfalls have been identified during Step 2, the RP has been receptive to feedback and committed to addressing them in future updates.

- Overall, I judge that the RP has put in place the necessary enabling factors to support an effective programme of HFI within the nuclear safety regime. I also welcome the commitment to consider the HF aspects of other E3S domains within scope. However, there remains work to be done to understand any differences in HF needed to support these other domains and demonstrate proportionality and suitability.

    - Substantiation of Human Based Safety Claims

- This section describes my assessment of the RP’s work to date to substantiate the human based safety (E3S) claims on the Rolls-Royce SMR design.

- ONR expects (SAP EHF.3 ref. [6]) that a systematic approach should be taken to identify human actions that can impact safety for all permitted operating modes and all fault and accident conditions identified in the safety case, including severe accidents. IAEA impose similar requirements, i.e., Requirement 32: Design for Optimal Human Performance (ref. [24]) and Requirement 11: Assessment of human factors (ref. [26])

- Once identified, proportionate analysis should be carried out of all tasks important to safety and used to justify the effective delivery of the safety functions to which they contribute (SAP EHF.5 ref. [6]).

- Further, ONR expects (SAP ESS.8 ref. [6]) that, for all fast-acting faults (typically less than 30 minutes) safety systems should be initiated automatically and no human intervention should then be necessary to deliver the safety function(s).  Where human intervention is needed to support a safety system following the start of a requirement for protective action, then the timescales over which the safety system will need to operate unaided, before intervention, should be demonstrated to be sufficient (SAP ESS.9 ref. [6]).

- In this section I consider whether:

- The identification of HBSCs is being carried out effectively.

- The role of the operator is being optimised.

- The human contribution to risk is understood.

- Due to the design and safety analysis maturity, I have not been able to sample individual HRAs or task analyses as they do not yet exist.

#### Evidence of identification of HBSCs

- I sampled the fault schedule (ref. [54]) to confirm whether HBSCs are being captured. There is evidence of capture across faults and hazards, but as the fault schedule is currently still quite immature, there is room for improvement as within the presentation of HBSCs, it is not always clear how and where these are being performed. The RP notes it has work to do in this area, and I will follow this up during Step 3.

- The scope of HBSCs and Human Failure Events (HFEs) modelling within the PSA is assessed in more detail within ONR’s PSA Assessment Report (ref. [55]) so I have not duplicated this effort.

- Identification of other important human actions from the other E3S domains are outside the scope of my assessment. The various approaches are considered within the respective regulatory assessments.

- At this stage of a GDA, I would expect the RP to be actively populating the PSA with operator actions and errors, which I can confirm (ref. [39]) is occurring.

- However, the L1 PSA only currently contains Type C errors (those that occur during fault responses), although the intention (ref. [39]) is that Types A and B will be incorporated when the design detail supports their inclusions.

- Considering the PSA maturity, the HF team has elected to utilise relatively conservative HEP screening data at 1.00 × 10-02 to provide some degree of useful risk insight, whilst not skewing the balance of protection to the point where it adversely influences the design.

- To date 430 HBSCs have been identified from the fault schedule, PSA, and HF initiated Tabular Task Analyses, which break down as follows:

- Type A - EMIT errors: 23.

- Type B – Operator initiated errors: 74.

- Type C:

Type C1 – Preventative: 74

Type C2 – Protective: 213

Type C3 – Mitigative: 46.

- The RP is prioritising (reg. [32] its HRA programme based on risk sensitivity.  HEPs are split between Important and All-Remaining, with the priority focus being on important. These are selected based on the following criteria:

- ‘Important’. Where HEP are generated for individual events that contribute >1.00% to the overall Core Damage Frequency (CDF) across the SMR PSA risk models.

- ‘All Remaining’, where HEP are generated for individual events that contribute <1.00% to the overall CDF across the SMR PSA risk models.

- This prioritisation will also inform how HF supports PSA, DSA and wider safety assessment.

- Overall, I consider that the RP has made a good start in identifying the important HBSCs on the Rolls-Royce SMR design, but I note the significant programme of work ahead to satisfactorily complete the declared PSA/HRA programme for GDA. I also note the novel further classification of Type C responses between preventative actions, protective and mitigative. This may offer some early risk insights into the balance of protection on the design. It is a topic I will explore further during Step 3.

#### Concept of Operations and the role of the operator

- ONR expects (SAP EHF.5 ref. [6]) that proportionate analysis should be carried out of all tasks important to safety and used to justify the effective delivery of the safety functions to which they contribute.

- As previously discussed within section 4.2.1, of the 430 HBSCs identified (ref. [39]), none of these have been fully substantiated to date (ref. [40]). However, work in this area is progressing and the RP recognises the substantiation effort required during Step 3. It has commenced the process in line with its stated methods. Therefore, the conclusions that can be drawn with respect to substantiated operator claims are limited. This area will therefore be a key focus for Step 3.

- The RP also submitted a concept of operations report (ref. [34]) and one detailing the AoF work (ref. [36]) conducted to date. Following regulatory feedback on the lack of human role detail in both, the RP supplemented this information via risk summary report (ref. [39]) that attempted to characterise the human contribution to risk.

- The stated operational concept for the Rolls-Royce SMR is that safety will be delivered via a combination of by passive means and automated systems (ref. [39]). It will also be secure by design (outside the scope of my assessment). Optimisation of automated and human delivered functions is being managed by the RP’s AoF process.

- Based on the analysis in support of the RD7 maturity level, full automation is provided for the following systems and safety measures:

- Steam Generator System

- Reactor Coolant Pressurising System

- Reactor Coolant Pressure Relief System

- Reactor Coolant Cooling System

- Emergency Boron Injection

- Low Pressure Injection System

- Alternative Shutdown Function

- SCRAM

- Emergency Core Cooling

- With the operator playing a monitoring and Defence in Depth (DiD) role if one of the above (and its associated DiD systems) fails to initiate.

- There are no claimed requirements for human interventions within 30 minutes from within the Main Control Room (MCR) or within 60 minutes for local to plant actions. In fact, the RP claims that for the first 72 hours, there is no claim for local to plant operator actions to protect any Loss of Electrics, Intact Circuit Faults, or Loss of Coolant Accidents.

- After 72 hours, the actions anticipated relate to replenishment of consumables such as coolant and diesel fuel. It is, however, important to note that these claims remain unvalidated.

- I consider the RP’s concept of minimising the reliance on the operator for safety critical actions and extending the time to respond aligns with regulatory expectations (SAP EKP.2) – assuming that vigilance, situational awareness, and job satisfaction is not adversely affected. It is possible to remove the operator from the control loop too much such that it adversely affects fault responses where the operator is required to manually intervene. I will seek to confirm during Step 3 that the RP is actively considering this risk as the HFE design matures.

- Control and monitoring is carried out from within a Main Control Room, supported by a Supplementary Control Room in the event of the MCR no longer being a tenable control location. This conceptually aligns with modern standards. Details of the design and functionality are not available at Step 2, so I have not looked at these locations further in Step 2. Step 3 (ref. [73]) will include within the HF scope (if required for the implementation for an E3S important human action), preliminary designs for the:

- Main Control Room

- Supplementary Control Room

- Emergency Response Centre

- Technical Support Centre

- Operational Support Centre

- Access Control Point

- Security Control Centre

- Outage Control Centre

- Work Execution Centre

- Radioactive Waste Control Room

- Radiation Protection Control Centre

- Overall, I consider the RP’s aim to de-emphasise the safety role of the operator on the Rolls-Royce SMR design to meet with regulatory expectations (SAP EKP.2). I also note that the method being applied to do this is sensitive to the risks of over-automation and the potential detriments to human reliability in the event of automation failures.

- However, I consider there to be significant further work needed by the RP to fully understand the role that the operator will take for all operational states and faults. I do not consider this has been clearly communicated during Step 2. This is explicable as similar shortfalls exist within the wider PSA and the RP’s HF team could not have demonstrated a significantly better understanding given the design maturity at RD7. The RP will need to quickly develop a cogent and coherent understanding of the operator role during Step 3, and I will monitor progress in this area to ensure that the RP can substantiate important HBSCs.

#### Human contribution to risk

- In poorly optimised designs, the operator can be a significant contribution to risk. To understand this contribution holistically, an evolving safety case needs to present an aggregated view of the complex data within the suite of PSA and HRA analyses to show where any vulnerabilities may lie. Without such a holistic view, it can be difficult for the safety case users to understand general design vulnerabilities (to human error) and whether the balance of protection (human-technology) is appropriate, and thus target design and analysis resource appropriately.

- For Step 2, the RP has only provided level 1 PSA that includes initiating events for at power modes 1 and 2, for reactor-based faults. There are no faults for shutdown modes (3-6), and the fuel route and spent fuel pool are also not considered.

- Also omitted from the scope at Step 2 is hazards modelling for internal or external hazards and level 2 and 3 PSA modelling. This means that a significant programme of updates is required for the RP to meet their stated aim of a full scope PSA (ref. [55]). Consequently, sensitivity analysis conducted to understand the human contribution to risk must be seen in this context. The areas currently omitted are also those which can be particularly sensitive to human actions.

- The RP was also unable to provide details during Step 2 on those operator activities that were subject to higher dose levels. Once this data is available during Step 3, it will be used to inform my sample of operator actions for assessment.

- For step 2, I asked the RP to conduct sensitivity studies based on the currently available safety analysis information. The results were documented in Reference [39].

- Of relevance to my assessment was the following.

Table 1 – HEP sensitivity studies

| Sensitivity Study ID | Sensitivity Study Description | Core Damage Freq (Per Reactor Year) |
| --- | --- | --- |
| Current | All HEP set to 1.00 × 10-02 | 7.56 x 10-07 |
| 1 | All HEP set to failure 1.00 | 3.22 × 10-05 |
| 2 | All HEP set to 1.00 × 10-01 | 3.61 × 10-06 |
| 3 | All HEP set to 1.00 × 10-03 | 4.71 × 10-07 |

- Whilst no direct comparisons can be made at this stage against ONR’s numerical targets seven, eight and nine, the results in table 1 suggest that the Rolls-Royce SMR design should be capable of meeting them without requiring significant levels of operator reliability. However, at this stage, it is not possible to determine whether this will be the case for those human actions linked to the areas out of scope of Step 2. I will seek further information in Step 3 to enable comparisons against the numerical targets.

- The sensitivity analysis identified that the human contribution to risk is currently dominated (again noting the scope caveat) by 4 human errors. These comprise:

- Operators maintain diesel generator fuel tank levels beyond 72 hours – Fussell-Vesely Contribution - 33%

- Manual high pressure injection system configuration in case of steam generator tube rupture. Fussell-Vesely Contribution - 5%

- Manual Chemical Volume Control System Restart - Fussell-Vesely Contribution - 2%

- Manual High Pressure Injection System stop in case of Spurious High Pressure Injection System Initiation - Fussell-Vesely Contribution – 2 %

- The rest are below 1 percent or negligible.

- Subject to an appropriate HFI programme, I do not consider any of those activities pose a particular reliability challenge given they are simple actions without significant time pressure.

- I also asked the RP to do a similar sensitivity exercise for SSCs to determine whether any EMIT insights could be gained at this stage with respect to SSC vulnerabilities. I note that at this stage, there are no unusual results being identified. The top 10 list of SSCs (by Risk Achievement Worth) is as follows.

- Reactor shutdown scram fails on demand due to mechanical fault (2 or more rods fail to insert).*

- Hardwired Diverse Protection System Platform fails.*

- Reactor Protection System Platform fails.*

- Local Ultimate Heat Sink train 2 tertiary tank large external leak.

- Local Ultimate Heat Sink train 3 tertiary tank large external leak.

- Local Ultimate Heat Sink train 1 tertiary tank large external leak.

- Local Ultimate Heat Sink train 3 tertiary tank drainage isolation valve spuriously opens.

- Local Ultimate Heat Sink train 1 tertiary tank drainage isolation valve spuriously opens.

- Local Ultimate Heat Sink train 2 tertiary tank drainage isolation valve spuriously opens.

- Reactor shutdown scram fails on demand due to mechanical fault (1 or more rods fail to insert).*

- * super-component that represents the failure of larger groups of components or equipment. The super-component considers both hardware and software aspects (if applicable) and currently excludes input from sensors and power supplies that are modelled explicitly.

- As can be seen from the list, risk is dominated by loss of heatsink faults (LUHS tanks draining). Tank inspection should be a simple field operator task given sufficient access. Accessibility assessment is a feature of the declared HFI programme.

- The other SSCs relate mainly to reactor protection Control & Instrumentation. SSC failure (from sources other than EMIT) is outside the scope of HF but EMIT of C&I is within the declared HFI scope so will be considered in the RP’s future programme of work. Setting reactor protection limits is not an unusual task so well within the bounds of being able to be carried out reliably should the design of the system be subject to suitable HFI, which the declared scope suggests it should.

- Whilst the sensitivity analysis conducted does provide some confidence that the human contribution to risk is being managed, and it is being used to inform the HRA programme, I did note a lack of evidence showing that it is being used to inform the HFI programme to target those activities and SSCs that contribute the greatest risk. This may be an artifact of the PSA maturity, but I will follow this up during Step 3 to ensure that the HFI programme is suitably risk informed.

- To conclude, the lack of PSA (and therefore HRA) scope has undoubtedly affected the confidence that can be drawn with respect to human contribution to risk for Step 2. However, I am content that the RP has demonstrated that it understands how to conduct sensitivity analysis in HRA to provide useful risk insights. I also consider that it has made sufficient progress and understanding in this area to progress to Step 3. The limited sensitivity analysis has shown that for those HBSCs and SSCs within the current scope, the human contribution to risk appears managed and not excessive. Whether this position is maintained when the additional scope is included remains to be seen, but this will be followed up during Step 3.

- The RP did not submit any detailed HRAs during Step 2, so this is another area that will be followed up early in Step 3. That is, gaining regulatory confidence that the output of the HRA methods aligns with expectations.

- I was unable to explore the management of HBSCs within Fault Schedule (ref. [54]) with much detail during Step 2 as the information I needed came very late in Step 2. I was able to confirm that the Fault Schedule (ref. [54]) is capturing HBSCs, but I consider the current approach needs work to improve its utility as it is not always clear how a function is being delivered – operator vs engineered system. I consider this to be an artefact of a developing Fault Schedule and the RP recognises that improvements are necessary.

- However, of more concern is the current application of Categorisation and Classification to HBSCs. The purpose of a Categorisation and Classification process is to ensure that the importance of functions and the SSCs and HBSCs that deliver them is understood and of sufficient reliability. Based on my very limited assessment during Step 2, I have concerns that the RP may be over-classifying HBSCs. To date the RP has identified (RQ-01151 (ref. [53]) 221 Class 1 operator claims, which appears both excessive and incongruous with the degree of automation and passivity in the design. In discussion with the RP, I suspect that many of these claims are over-classified simply because they relate to the extended functioning of a Class 1 systems, either by replenishment of consumables, or by responding to failures. Whilst over-classification is no direct detriment to safety, it can obscure what is important for safety in amongst actions that are less so and lead to a design that is less optimised. For the RP it also potentially increases costs.

- I have started to follow this up at the end of Step 2 and it will be a key engagement early in Step 3.

#### Conclusions

- It is evident that the design and PSA maturity at Step 2 has made it challenging for the RP to present a robust case that the role of the operator is fully understood and optimised on the Rolls-Royce SMR during Step 2. This is expected as the design currently sits at concept level definition.

- However, the high degree of automation, human contribution to risk data, and operator response time requirements suggest (noting the scope limitations) that the design should be tolerant to human error.

- Whilst recognising this, at the current time the very high number (in comparison to other modern reactor designs) of Class 1 operator claims undermines this position. The RP recognises this is likely over-classification and is planning a review of its HBSC categorisation and classification approach. I am confident that this is a methodological issue rather than one of design optimisation, but I will make it a key focus during Step 3 to gain further assurance.

- Overall, I am content that the RP’s work on HRA generally meets ONR’s expectations as set out in NS-TAST-GD-063 (ref. [21]) for HRA and identification of HBSCs.

    - Human Factors Engineering

- This section describes my assessment of the RPs application of HFE to the design of the Rolls-Royce SMR.

- ONR expects (ref. [6]):

- A structured and systematic approach to the integration of HF into the design process (SAP EHF.1.).

- When designing systems, dependence on human action to maintain and recover a stable, safe state should be minimised. The allocation of safety actions between humans and engineered structures, systems or components should be substantiated. (SAP EHF.2.).

- Workspaces in which operations (including maintenance activities) are conducted should be designed to support reliable task performance. The design should take account of the physical and psychological characteristics of the intended users and the impact of environmental factors (SAP EHF.6.).

- Suitable and sufficient user interfaces should be provided at appropriate locations to provide effective monitoring and control of the facility in normal operations, faults and accident conditions (SAP EHF.7.).

- IAEA imposes similar requirements via Requirement 32 Design for Optimal Human Performance (ref. [24]) and provides specific guidance on HFE design in reference [27] (which ONR’s HFE related TAGs take account of).

- For Step 2, due to the design maturity (RD7), I have focussed my assessment on confirming that the RP’s HF team are suitably delivering HFI into the design, rather than on assessing whether the design meets HF RGP, as the detail to do this is not yet available.

- It would be disproportionate to repeat effort from Step 2 into Step 3 where it can be avoided.

- Consideration of the balance of safety function delivery is considered in section 4.2.1 above so not repeated here. In the Step 3 assessment report, the specific HFE carried out in support of safety functional delivery will be discussed here.

#### HFE support

Allocation of Function output

- To date, the RP has analysed 28 systems and 234 functions. As it typical in reactor design, the trend is to de-emphasise the safety role of the operator when it comes to directly responding to faults.

- At Step 2, ~ 62% of the assessed functions have been allocated to being delivered automatically. This includes the following systems and safety measures:

- Steam Generator System

- Reactor Cooling Pressurising System

- Reactor Cooling Pressure Relief System

- Reactor Cooling System

- Emergency Boron Injection

- Low Pressure Injection System

- Alternative Shutdown Function

- SCRAM

- Emergency Core Cooling

- 9% of the assessed functions are allocated as full manual (local or remote) tasks for the following systems:

- Cooling Tower System,

- Chemistry Control System.

- ~ 29% of the assessed functions are allocated to operator-initiated automation, predominantly (21%) through operator-initiated sequence automation for systems including:

- Processing & Treatment System for Liquid Effluent

- Drains

- Solid Radioactive Waste Storage System

- 66 additional functions across 13 systems have been assessed since RD6, with associated implementation advice provided to system owners, showing good progress in the RP’s analysis.

- Given that the design is still at the concept phase, and little implementation detail exists with respect to feedback to the operator, I was unable to assess whether the functional allocations are suitably optimised. Conceptually, they have face validity, as reactor fault protection is largely achieved via automatic systems, whilst the operator still retains the ability to initiate plant shutdown on the detection of a failure or hazard and to manually initiate a safety function in the event of a system failure. I will monitor AoF progress during Step 3 and sample a representative range of decision records to confirm the logic of the decisions and the subsequent adequacy of the implementation of the function.

HAZOP and SWIFT support

- To date, the RP’s HF team have supported the 49 HAZOPS (Hazard and Operability Studies) and SWIFT (Structured What If Technique) reviews (List provided in appendix 2) .

- It is positive that the HF team are being engaged early in the safety analysis process, and that they have attended a significant number of these reviews.

HF in decision records

- As the output of these workshops was not submitted for assessment, I sampled several of the few decision records (which capture the RP’s optioneering reviews) submitted during Step 2 to confirm the degree of actual documented HFI into the SMR’s SSCs:

- R01 – 501 – Fuel Storage Requirements and Strategy

- RI-99 Cask Loading Definition Decision Record

R01-538 – FAA – system layout – decision record

- R01-523 – System Architecture for AxSS [KUB] & PERMS [KUK] Reactor Island Sampling Systems – Decision Record

- From my sample I did not find evidence of systematic HFI input into the decision-making process. Issue noted comprised:

- Lack of HF SQEP support.

- Future HF work required in support of the development of the design was poorly (or not) scoped.

- A focus on operations at the cost of the potential human impact to EMIT errors

- I consider this a shortfall against ONR expectations to suitably integrate human factors within the design and assessment (SAP EHF.1). These shortfalls may be indicative of a process bedding in given the dates on the submissions, so I will monitor HFI within the decision record process as a residual matter during Step 3.

HF in design checklists

- As the design progresses beyond optioneering, and a decision is made on a specific option or technology, the RP uses the DOORS system (discussed in section 4.2.1) to ensure that the design of the SSC meets its requirements.

- To confirm that this process is working effectively to deliver suitable and sufficient HFI, I sampled the completed DOORS requirements checklist (ref. [44]) for the Steam Generation System, and found that:

- The checklists do drive the consideration of HF at the system level.

- There were similar scope omissions as per the style guide (see section 4.2.1).

- Evidence presented in the completed checklist was insufficient to substantiate that the consideration / requirement was fully met. It also included many promissory statements with no indication whether these were then captured in RAIDO.

- Given the checklist includes within scope the Steam Generators, there was little detail captured in relation to inspection and the equipment facilitating those tasks.

- I consider there is work to do this area to ensure suitable and sufficient incorporation of HF RGP. Work is needed to improve the scope of requirements and the degree of evidence captured showing compliance. I will follow this up in Step 3.

Control locations

- The RP did not submit any detailed HF design evidence for the control locations during Step 2 as it was not available due to the maturity of the design. For example, at Step 2, the RP is still conducting task analysis (ref. [40]) to inform the design of the MCR and its associated C&I requirements. I will consider the adequacy of the control location designs during Step 3.

- However, it is worth noting that the RP has identified what I consider to be a highly comprehensive scope of control locations that will be subject to future HFI (not all of these locations will be developed during the GDA). The scope (ref. [37]) comprises the following.

- Control location Main Control Room

- Supplementary Control Room

- Emergency Response Centre

- Technical Support Centre

- Operational Support Centre

- Access Control Point

- Security Control Centre

- Outage Control Centre

- Work Execution Centre

- Radioactive Waste Control Room

- Radiation Protection Control Centre

- Off-site Emergency Response Centre

- Off-site Technical Support Centre

- Control Stations

- Localised Control & Monitoring.Assessment.

#### Conclusions

- To conclude, the maturity of the RR SMR has meant that the RP has not been able to fully demonstrate the efficacy of its HFE process.

- The scope of AoF and HAZOP/SWIFT support is positive as are the RP’s ambitions for embedded HFE requirements within its internal design requirements processes.  However, I consider there is significant work to do this area to ensure suitable and sufficient incorporation of HF RGP. Further, work is needed to improve the scope of requirements within DOORs and the degree of evidence captured showing compliance. I will follow this up in Step 3.

    - ALARP

- Under health and safety law, duty holders are required to reduce risk so far is reasonably practicable. At the point where reasonable practicality is considered to be achieved, ONR consider that risks have been reduced As Low As Reasonably Practicable (ALARP).

- This is done primarily via the dutyholder’s demonstration of meeting established RGP, and where this is not possible, for example, where novel technologies are being considered, then duty holders are expected to adopt a computational first principles approach, which appropriately balances sacrifice vs risk. More extensive testing, use of research data and V&V may also be required to provide the necessary assurance.

- The RP has the concept of ALARP embedded into its primary claim for HF: “Human Factors is integrated into the design based on sound safety principles and methods that minimise risks to ALARP”.

- With respect to meeting RGP, it is not possible to conclude either way at this stage. The RP has established methods that range from exceeding RGP, to requiring further work.

- Of the guidance and requirements selected to date, I consider they generally meet RGP, but are incomplete in scope so further work is required in Step 3 (see section 4.2.1 above).

- Full comparison against ONR’s numerical targets (see section 4.2.2 above) is not practical at this stage due to the maturity of the HRA, but sensitivity analysis to date reflects positively on the design and raises no significant issues with respect to human contribution to risk.

- With respect to computational first principles (see section 4.2.1 and 4.2.3 above), I consider that whilst the RP has established systems that do encourage the consideration of HF, their application to date has been inconsistent and therefore the integration not always adequate.

- To conclude, I consider that the RP has in place all the necessary mechanisms in place to deliver a design that can be judged ALARP and has shown progress in this area. Unsurprisingly for Step 2, there remains significant further work to do in this area for a judgement that the design reduces risk ALARP to be made.

    - E3S consistency

- ONR expects (ref. [17]) that the safety case should, amongst other things, be cogent, coherent, and internally consistent. Given that the Tier 1 E3S case has been revised during Step 2, I assessed whether the updates were generally consistent with the Tier 2 and 3 submissions for HF.

- Chapter 18 (ref. [3]) of the E3S case is the one presenting the wider HF case. The updates to the CAE structure I consider to be an improvement, and because it currently summarises mostly scope and RP arrangements information, and these haven’t changing significantly, I found it to be internally consistent with the Tier 2 and 3 material submitted to date.

# Conclusions

- This report presents the Step 2 HF assessment for the GDA of the Rolls-Royce SMR design. The focus of my assessment in this Step was the fundamental adequacy of the design and E3S case. I have assessed the Tier 1 E3S chapters and relevant supporting documentation provided by Rolls-Royce SMR Limited to form my judgements. I targeted my assessment, in accordance with my assessment plan (ref. [10]), at the content of most relevance to HF against the expectations of ONR’s, TAGs and other guidance which ONR regards as relevant good practice.

- Based upon my assessment, I have concluded the following:

- There are no fundamental issues identified to date with the HF elements of the: process and organisational enablers for HFI, the Rolls-Royce SMR design, and the E3S case, that I conisder to be prejudicial to the RP entering Step 3.

- The Rolls-Royce SMR design features very few novel concepts that are likely to challenge the ability of the operator to safely and securely operate it. The ‘small’ characteristic of an SMR design could pose a risk to EMIT activities due to the reduced plant footprint, but in recognition of this risk, the RP has introduced advanced human CAD tools to identify and design out (or mitigate) contested space.

In terms of capability, I consider the RP’s HF team to be suitably competent to have developed a modern standards HFI programme for Step 2. The RP is committed to securing additional resource for Step 3 and I will monitor delivery progress and quality as a residual matter.

- I consider the scope of HFI for nuclear safety to meet RGP. However, at Step 2, the RP has provided insufficent material to conclude the same for HFI scope in the following domains: Conventional Health and Safety; Security; Safeguards and Environment. The RP recognises that further work in these domains is required and I will monitor progress in the RP’s scope development during Step 3 as residual matters. Assessingapplication of HF in these areas during Step 3 is outside of my assessment scope, but I will raise the need for this with ONRs assessment leads and with Inspectors in the respective areas.

- I consider that the methods and approaches that the RP has put in place for suitable and sufficient HFI meet, are close to meeting, or exceed, RGP. The RP is aware of those areas where further work is required and is actively working on these during the final stages of Step 2 and where necessary will be taking them forward as part of Step 3. I will monitor progress during Step 3 as residual matters.

- I consider the HF RGP selected for the Rolls-Royce SMR design broadly meets regulatory expectations but note that further work is required in this area as it is currently incomplete, especially in the area of identifying specific legal requirements such as LOLER and PUWER, and regime specific legal requirements and approaches in the areas of Secuirty, Safegaurds and Environment. The RP recognises these shortfalls and is updating the design guidance, which will be reissued during Step 3. I will follow this up during Step 3 as residual matters to ensure that the RGP selected supports the demonstration of ALARP for nuclear safety (as far as is practicable within GDA).

- Whilst the HFI enablers generally meet RGP, the evidence that the arangements are being used as intended does not fully support the primary E3S claim that “Human Factors is integrated into the design based on sound safety principles and methods that minimise risks to ALARP”. I found several shortfalls in expectations with respect to HF representation in optioneering and design reviews which RR have committed to address moving forward.

- The RP has established a suitable approach to determine an optimised balance between engineered systems and human delivery of functions – noting that evidence of application to Environment, Security and Safegaurd domains was not submitted in Step 2. I will monitor the inclusion of the full scope of the E3S in the AoF process during Step 3, but my focus will remain nuclear safety. Other disciplines will consider the adequacy of the AoF decision making for their areas. I will also sample a range of AoF decisions to ensure that they have adequately followed the RP’s declared process, and any subsequent HFE work supporting the implementation of the function.

- The RP has established a generally suitable approach for the identification of HBSCs. Further, there is evidence that these are being captured in both the PSA and the Fault Schedule. However, I note an over-classification of HBSCs such that the RP is reporting an extremely high number of Class 1 operator claims for at power operations. The RP recognises this and will be revising its approach early in Step 3.

- HRA data currently used is based on simplistic, but conservative, screening HEPs, and US sourced IEF data. Given the design maturity I consider this appropriate but note it will need significant work in this area to be considered a) best estimate, and b) part of a suitable and sufficient risk assessment that includes propportionate task and error analysis, comprises all error types (inc. errors of commission), and appropriately considers violations. I will monitor progress in this area during Step 3 as a residual matter.

- The RP has established generally suitable approaches for HFE, but there is evidence that these systems are not being adequately applied by non HF SQEPs. I will follow this up during Step 3 as a residual matter.

- The RP has provided insufficient evidence at Step 2 that the scope, and incorporation within the design, of Operational Experience and Learning within the HF domain is adequate. I note that the RP is aware of this and has been carrying out remedial work during Step 2. I will follow this up during Step 3 as a residual matter.

- Overall, based on my assessment to date, and subject to the provision and assessment of suitable and sufficient supporting evidence, I have not identified any fundamental safety shortfalls that could prevent ONR permissioning the construction of a power station based on the generic Rolls-Royce SMR design.

  - Recommendations

- My recommendations are as follows:

- Recommendation 1: ONR should consider the outcomes from my assessment as part of the decision to progress to Step 3 of GDA for the generic Rolls-Royce SMR design.

# References

| [1] | Rolls-Royce SMR Limited, Environment, Safety, Security and Safeguards Case Version 2, Tier 1, Chapter 1: Introduction, SMR0004294, Issue 3, May 2024. (Record ref. ONRW-2019369590-9881). |
| --- | --- |
| [2] | Rolls-Royce SMR Limited, Environment, Safety, Security and Safeguards Case Version 2, Tier 1, Chapter 13: Conduct of Operations, SMR0004247, Issue 3, May 2024. (Record ref. ONRW-2019369590-9919). |
| [3] | Rolls-Royce SMR Limited, Environment, Safety, Security and Safeguards Case Version 2, Tier 1, Chapter 18: Human Factors Engineering, SMR0004520, Issue 3, May 2024. (Record ref. ONRW-2019369590-9908). |
| [4] | Rolls-Royce SMR Limited, Environment, Safety, Security and Safeguards Case Version 2, Tier 1, Chapter 24: ALARP Summary, SMR0004487, Issue 3, May 2024. (Record ref. ONRW-2019369590-9914). |
| [5] | ONR, Guidance on Mechanics of Assessment, NS-TAST-GD-096, Issue 1.2, December 2022. www.onr.org.uk/media/documents/guidance/ns-tast-gd-096.docx. |
| [6] | ONR, Safety Assessment Principles for Nuclear Facilities (SAPs), 2014 Edition, Revision 1, January 2020. www.onr.org.uk/media/pobf24xm/saps2014.pdf. |
| [7] | ONR, Technical Assessment Guides. www.onr.org.uk/publications/regulatory-guidance/regulatory-assessment-and-permissioning/technical-assessment-guides-tags/nuclear-safety-tags/technical-assessment-guides-tags-nuclear-safety-full-list/. |
| [8] | ONR, Guidance on the Production of Reports for Permissioning and Assessment, NS-TAST-GD-108, Issue No. 1, December 2022. (Record ref. 2022/71935). |
| [9] | ONR, New Nuclear Power Plants: Generic Design Assessment Guidance to Requesting Parties, ONR-GDA-GD-006, Revision 0, October 2019. www.onr.org.uk/media/pylbvfnz/onr-gda-gd-006.pdf. |
| [10] | ONR, Step 2 Human Factors Assessment Plan for the Generic Design Assessment of the Rolls-Royce SMR, ONR-GDA-AP-22-020, Issue No. 1, March 2023. (Record ref. ONRW-2126615823-425). |
| [11] | ONR, Generic Design Assessment of the Rolls-Royce SMR - Step 2 summary, Issue No. 1, July 2024. (Record ref. ONRW-2019369590-8980). |
| [12] | Rolls-Royce SMR Limited, Rolls-Royce SMR Generic Design Assessment Scope, SMR0002183, Issue 2, January 2023. (Record ref. ONRW-2019369590-8058). |
| [13] | IAEA, Safety Standards. www.iaea.org. |
| [14] | IAEA, Nuclear Security series. www.iaea.org. |
| [15] | WENRA, Safety Reference Levels for Existing Reactors 2020. February 2021. WENRA. www.wenra.eu. |
| [16] | WENRA, WENRA Safety Objectives for New Nuclear Power Plants and WENRA Report on Safety of new NPP designs - RHWG position on need for revision. September 2020. www.wenra.eu. |
| [17] | ONR, The purpose, scope and content of safety cases, NS-TAST-GD-051, Issue 7.1, December 2022. www.onr.org.uk/media/documents/guidance/ns-tast-gd-051.docx. |
| [18] | ONR, Human Factors Integration, NS-TAST-GD-058, Issue 5, March 2023. www.onr.org.uk/media/documents/guidance/ns-tast-gd-058.docx. |
| [19] | ONR, Human Machine Interfaces, NS-TAST-GD-059, Issue 5.2, December 2022. www.onr.org.uk/media/documents/guidance/ns-tast-gd-059.docx. |
| [20] | ONR, Workplaces and Work Environment, NS-TAST-GD-062, Issue 4.2, April 2023. www.onr.org.uk/media/documents/guidance/ns-tast-gd-062.docx. |
| [21] | ONR, Human Reliability Analysis, NS-TAST-GD 063, Issue 6, December 2022. www.onr.org.uk/media/documents/guidance/ns-tast-gd-063.docx. |
| [22] | ONR, Allocation of Function between Human and Engineered Systems, NS-TAST-GD-064, Issue 5, May 2023. www.onr.org.uk/media/documents/guidance/ns-tast-gd-064.docx. |
| [23] | IAEA, Format and Content of the Safety Analysis Report for Nuclear Power Plants, Specific Safety Guide No. SSG-61, September 2021. www.iaea.org. |
| [24] | IAEA, Safety of Nuclear Power Plants: Design, Specific Safety Requirements No. SSR-2/1 (Rev. 1), February 2016. www.iaea.org. |
| [25] | IAEA, Commissioning and Operation of Nuclear Power Plants, Specific Safety Requirements No. SSR-2/2 (Rev. 1), February 2016. www.iaea.org. |
| [26] | IAEA, Safety Assessment for Facilities and Activities, General Safety Requirements No. GSR Part 4 (Rev. 1), February 2016. www.iaea.org. |
| [27] | IAEA, Human Factors Engineering in the Design of Nuclear Power Plants, IAEA Safety Standards Series No. SSG-51, 2019. www.iaea.org. |
| [28] | Rolls-Royce SMR Limited, E3S CAE Route Map, SMR0002155, Issue 3, November 2023. (Record ref. ONRW-2019369590-8059). |
| [29] | Rolls-Royce SMR Limited, Human Factors Integration Plan for the RR Small Modular Reactor, SMR0000219, Issue 1, April 2023. (Record ref. ONRW-2019369590-2681). |
| [30] | Rolls-Royce SMR Limited, RR SMR HMI Style Guide, SMR0003911, Issue 1, January 2023. (Record ref. 2023/7774). |
| [31] | Rolls-Royce SMR Limited, RR SMR Target Audience Description, SMR0003975, Issue 2, April 2024. (Record ref. ONRW-2019369590-9756). |
| [32] | Rolls-Royce SMR Limited, RR SMR Human Reliability Analysis: Quantitative Assessment Strategy, SMR0004028, Issuel 1, January 2023. (Record ref. 2023/7770). |
| [33] | Rolls-Royce SMR Limited, RR SMR Human Reliability Analysis Strategy, SMR00004366, Issue 1, February 2023. (Record ref. ONRW-2019369590-2721). |
| [34] | Rolls-Royce SMR Limited, RR SMR Concept of Operations, SMR0005048, Issue 1, March 2023. (Record ref. 2023/19876). |
| [35] | Rolls-Royce SMR Limited, Human Factors Programme, SMR0005544, Issue 1, April 2023. (Record ref. 2023/26310). |
| [36] | Rolls-Royce SMR Limited, Allocation of Function Summary, SMR0005768, Issue 2, December 2023. (Record ref. ONRW-2019369590-5825). |
| [37] | Rolls-Royce SMR Limited, Rolls-Royce SMR Control Facilities Description, SMR0005883, Issue 2, December 2023. (Record ref. ONRW-2019369590-5824). |
| [38] | Rolls-Royce SMR Limited, Human Reliability Analysis Progress Report, SMR0006534, Issue 1, July 2023. (Record ref. ONRW-2019369590-3616). |
| [39] | Rolls-Royce SMR Limited, Human Factors Risk Summary, SMR0009127, Issue 1, January 2024. (Record ref. ONRW-2019369590-6565). |
| [40] | Rolls-Royce SMR Limited, SMR Task Analysis Progress Report, SMR0009105, Issue 1, December 2023. (Record ref. ONRW-2019369590-5823). |
| [41] | Rolls-Royce SMR Limited, Human Factors Engineering Summary, SMR0009395, Issue 1, January 2024. (Record ref. ONRW-2019369590-6564). |
| [42] | ONR, Level 4 Human Factors - General KIT meeting - 28 November 2023, ONR-NR-CR-23-449, November 2023. (Record ref. ONRW-2029369590-5714). |
| [43] | British Standards Institute, BS EN 61839:2014: Nuclear power plants – Design of control rooms – Functional analysis and assignment. www.bsigroup.com. |
| [44] | Rolls-Royce SMR Limited, Human Factors Checklist - Guidance and Process, SMR0004379, February 2024. (Record ref. ONRW-2019369590-7198). |
| [45] | EEMUA, Alarm Systems: A Guide to Design, Management and Procurement, Publication 191, Edition 3. eemua.org. |
| [46] | HM Government, The Lifting Operations and Lifting Equipment Regulations 1998, www.legislation.gov.uk/uksi/1998/2307/contents/made. |
| [47] | HM Government, The Provision and Use of Work Equipment Regulations 1998. www.legislation.gov.uk/uksi/1998/2306/contents/made. |
| [48] | ONR, RR SMR Human Factors Level 4, ONR-NR-CR-23-240, 25 July 2023. (Record ref. ONRW-2019369590-3922). |
| [49] | U.S. Nuclear Regulatory Commission, Rates of Initiating Events at U.S. Nuclear Power Stations: 1987 - 1995, NUREG/CR-5750, ww.nrc.gov. |
| [50] | Handbook of human-reliability analysis with emphasis on nuclear power plant applications, NUREG/CR-1278, Final report, August 1983, www.nrc.gov. |
| [51] | J. Williams, Human Error Assessment Reduction Technique - Proposed Method for Assessing and Reducing Human Error. 9th Advances in Reliability Technology Symposium, 1986. |
| [52] | US Nuclear Regulatory Commission, Standardised Plant Analysis Risk – HRA (SPAR-H), NUREG/CR-6883, www.nrc.gov. |
| [53] | ONR, Schedule of Step 2 Regulatory Queries, April 2024. (Record ref. ONRW-2019369590-9071). |
| [54] | Rolls-Royce SMR Limited, Fault Schedule Module - Version 7, SMR0004916_002, January 2024, (Record ref. ONRW-2019369590-7454). |
| [55] | ONR, Generic Design Assessment of the Rolls-Royce SMR - Step 2 assessment of Probabilistic Safety Analysis, Issue No. 1, June 2024. (Record ref. ONRW-2126615823-2692). |

Appendix 1 – Relevant SAPs considered during the assessment

| SAP No. | SAP Title |
| --- | --- |
| MS.2 | Capable Organisation |
| MS.4 | Learning |
| EHF.1 | Integration within design, assessment and management |
| EHF.2 | Allocation of safety actions |
| EHF.3 | Identification of actions impacting safety |
| EHF.5 | Task analysis |
| EHF.6 | Workspace design |
| EHF.7 | User interfaces |
| EHF.10 | Human reliability |
| EHF.11 | Staffing levels |
| ECS.2 | Safety classification of structures, systems and components |
| SC.4 | Safety case characteristics |
| ESS.8 | Automatic initiation |

# Appendix 2 – HF HAZOP / SWIFT attendance

System

Reactor Island

Automatic Depressurisation

Chemistry and Volume Control System

Cold Shutdown Cooling System

Component Cooling System

Control Rod Ejection

Emergency Boron Injection

Emergency Core Cooling System

Fuel Assembly Cleaning System

Fuel Handling in Containment

Fuel Pool Cooling System Fuel Pool Purification System Fuel Pool Supply System

Fuel Transfer System

New Fuel Receipt and Inspection

Intermediate Level Waste Temporary Storage (Reactor Island Waste Systems)

Liquid Effluent Gaseous Effluent Liquid Drain

Low Pressure Injection System

Main Access Hatch Personnel Airlock

Mechanical Handling In Containment

Passive Decay Heat Removal Passive Steam Condensing System Local Ultimate Heat Sink

RC Sampling Gaseous Media

Severe Accident Depressurisation

Small Leak Injection System

Steam Generator Support Systems

Alternative Shutdown Function

Common System for Cooling Water

RI Component Decontamination System

Containment

Containment Cooling and Spray Function

Containment Hydrogen Management System

Demin Water and Wastewater

Electrical Power Systems

Low Voltage Uninterruptible Power Supply

Essential Service Water System

In Containment Overhead Crane

In-Vessel Retention

Reactor Coolant Pressurising System

Reactor Coolant Pressure Relief

RC Nuclear Sampling System Gaseous Media Sampling System

Reactor Coolant System Steam Generator RC Pumps RC Pipework

Reactor Systems

Auxiliary Sampling Process & Emissions Radiation Monitoring Post Accident Sampling

Scram

Site Layout

Spent Fuel Storage / Cask Loading

Steam Generator Blowdown

Test Rig 01 Core Flow

Turbine Island

Foundation Frame and Support Structure (Turbine Support Structure)

Auxiliary Steam Generating and Supply system

External Hazards