Office for Nuclear Regulation (ONR)
Site Report for
Hinkley Point B Site

Report for period 1 July to 30 September 2022

Foreword
This report is issued as part of ONR's commitment to make information about inspection and regulatory activities relating to the above site available to the public. Reports are distributed to members for the Site Stakeholder Group and are also available on the ONR website (http://www.onr.org.uk/llc/).
Site inspectors from ONR usually attend Site Stakeholder Group meetings where these reports are presented and will respond to any questions raised there. Any person wishing to inquire about matters covered by this report should contact ONR.

Table of Contents

Inspections
  1. Dates of Inspection
The ONR site inspector and specialist inspectors made inspections on the following dates during the report period:
- 23 to 25 August 2022 (Electrical, Chemistry, Operating Rules and operating Instructions)
- 9th September 2022 (Operating Rules and Operating Instructions follow up)

Routine Matters
  1. Inspections
Inspections are undertaken as part of the process for monitoring compliance with:
- the conditions attached by ONR to the nuclear site licence granted under the Nuclear Installations Act 1965 (NIA65) (as amended);
- the Energy Act 2013
- the Health and Safety at Work etc Act 1974 (HSWA74); and
- regulations made under HSWA74, for example the Ionising Radiations Regulations 2017 (IRR17) and the Management of Health and Safety at Work Regulations 1999 (MHSWR99).
The inspections entail monitoring the licensee’s actions on the site in relation to incidents, operations, maintenance, projects, modifications, safety case changes and any other matters that may affect safety. The licensee is required to make and implement adequate arrangements under the conditions attached to the licence in order to ensure legal compliance. Inspections seek to judge both the adequacy of these arrangements and their implementation.
In this period, routine inspections of Hinkley Point B Power Station covered the following:
Electrical
The inspection focused on the arrangements that have been established in compliance with three specific topic areas and their implementation:
Conventional electrical safety
Reactor (R) 4 pre-defueling outage electrical engineering activities
The electrical isolation of R3 control rods.
From this inspection it was evident that EDF Energy HPB:

Has adequate arrangements for carrying out electrical work, including work planning, risk assessment, safety rules, competence of staff, selection and use of equipment, supervision arrangements, monitoring and management arrangements, in accordance with Electricity at Work Regulations 1989 and the Health and Safety at Work Act, and that they were adequately implemented.
Notwithstanding this, during the inspection EDF Energy NGL were unable to adequately demonstrate that electrical testing of lighting and small power installations had been undertaken within the HPB main reactor building in accordance with IET publication BS7671 Requirements for electrical installations and the guidance within the EDF Energy NGL TGN 064, and therefore demonstrate compliance with the Electricity at Work Regulations 1989. Based on this finding the inspector rated the inspection as AMBER - seek improvement - against the conventional electrical safety inspection.
As a result of the compliance shortfalls, a fleet wide regulatory issue was raised in order to address any shortfalls in compliance with the Electricity at Work Regulations 1989 and the Health and Safety at Work Act. The issue was raised fleet wide due to similar findings at Dungeness B and Hunterston B.
EDF demonstrated adequate arrangements for the R4 pre-defueling outage activities, including inspection and observation of the actual condition of the station’s electrical Safety Systems and Components (SSCs), SSCs system health, progress against the station’s pre-defueling outage plan, management of emergent issues and completion of work order cards, in accordance with licence condition 28, and that they were adequately implemented. It was therefore the inspector’s opinion that this inspection is rated as Green against licence condition 28 (examination, inspection, maintenance and testing) - no formal action required.
EDF demonstrated adequate implementation of the arrangements for the electrical isolation of R3 control rods, including inspection and observation of control rod isolations, a demonstration of the complete auditable trail of documentary evidence from a single isolation and positive confirmation that R3 control rods cannot be electrically driven from the reactor, in accordance with licence condition 22. It was therefore the inspector’s opinion that this inspection be rated as Green against licence condition 22 (modification or experiment on existing plant) - no formal action required.
Chemistry
This was one in a series of reactor chemistry inspections conducted at each EDF Nuclear Generation Ltd (NGL) site approximately every three years. The focus of these inspections is on operational chemistry control and management. This inspection was carried out by an ONR specialist inspector jointly with the Environment Agency and specifically considered:
- technical governance implementation of station operating rules and instructions (particularly focusing on chemistry control of feedwater (off-load) and the ponds); and
- chemistry requirements, the ability to maintain the relevant plant and how plant health is assessed (with duties for end of generation considered).
The inspection considered the following Licence Conditions (LCs) in relation to pond chemistry and off-load boiler chemistry:
LC 23 (Operating Rules)
The implementation of control parameters for pond chemistry and off-load boiler chemistry was reviewed, identifying appropriate visibility of control parameters from technical governance in station documentation. Evidence of control of pond and off-load boiler chemistry was also sampled. Station was able to demonstrate good compliance with chemistry control parameters with only minor deviations observed and adequately addressed.

Based on the sample, the inspector was content station was controlling chemistry in line with the requirements of the safety case and therefore judged a rating of Green (no formal action) to be appropriate for LC 23.
LC 28 (Examination, Inspection, Maintenance and Testing)
The inspector sampled the station’s arrangements for maintaining feedwater plant availability, and undertook a walkdown of parts of the system. The inspector identified relatively few defects on the system, with higher priority defects either addressed or within permitted repair timescales. The inspector sampled maintenance records in more detail, identifying no issues.

Based on the sample, The inspector judged a rating of Green (no formal action) to be appropriate for LC 28.
Operating Rules and Operating Instructions
This intervention was undertaken as part of a series of planned interventions that are listed in the HPB Integrated Intervention Strategy 2022/2023. The intervention was not completed during the report period and its findings will be reported in the next SSG report.

Non-Routine Matters
Licensees are required to have arrangements to respond to non-routine matters and events. ONR inspectors judge the adequacy of the licensee’s response, including actions taken to implement any necessary improvements.
Incorrect Isolation of Differential Pressure Switch
During maintenance of a dome differential pressure switch the switch was found isolated and would not operate, if required. This pressure switch is designed to prevent damage to the gas circulator if there is a substantial differential pressure across the circulator dome during opening operations. The gas circulators are safety mechanisms under the operational and defueling safety case.
The significance is reasonably low from a direct safety consequence. The reactor remains in a safe condition if one of the gas circulators is lost and the most likely impact would have been a delay to defuelling. It is noted, however, that had any damage happened during defuelling then the defuelling safety case does not allow for the gas circulators to be removed and that any significant repair would require a revised safety case.
ONR will await the outcome of the licensee’s internal investigation before any further decisions are made.
# Charge Machine light load modification
The Engineering Change documentation for the charge machine light load modification required a test on an interlock to be carried out prior to defuelling operations commencing. This test had not been specifically included in the commissioning test schedule. It was discovered that the test had been completed, due to routine maintenance, but this was not known when the first two fuel stringers were discharged from the reactor.
Although the safety impact from this incident is minimal, as the checks had been carried out, the failure to adequately transcribe safety case requirements into the commissioning requirements indicates an issue with the dutyholder's arrangements, or their implementation. Because of the significant amount of modifications ongoing at this stage on the site this will be followed up by the site inspector when the dutyholder investigation has been completed.
Regulatory Activity
ONR may issue formal documents to ensure compliance with regulatory requirements. Under nuclear site licence conditions, ONR issues regulatory documents, which either permit an activity or require some form of action to be taken; these are usually collectively termed ‘Licence Instruments’ (LIs) but can take other forms. In addition, inspectors may take a range of enforcement actions, to include issuing an enforcement notice. No licence instruments or enforcement action was taken during this period.
News from ONR
For the latest news and information from the Office for Nuclear Regulation, please read and subscribe to our regular email newsletter ‘ONR News’ at www.onr.org.uk/onrnews

Contacts
Office for Nuclear Regulation
Redgrave Court
Merton Road
Bootle
Merseyside
L20 7HS
website:	www.onr.org.uk
email:	Contact@onr.gov.uk
This document is issued by the Office for Nuclear Regulation (ONR). For further information about ONR, or to report inconsistencies or inaccuracies in this publication please visit http://www.onr.org.uk/feedback.htm.
© Office for Nuclear Regulation 2022
If you wish to reuse this information visit www.onr.org.uk/copyright.htm for details.
Published 02/23
For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled.