Dungeness B Power Station - Initial Defuelling Safety Case

Assessment of NP/SC 7813 Dungeness B Power Station - Initial Defuelling Safety Case, EC No: 369274 Revision 000

Project Assessment Report ONR-OFD-PAR-22-007
Revision 0
8 December 2022

## © Office for Nuclear Regulation, 2023
## If you wish to reuse this information visit www.onr.org.uk/copyright for details.
## Published 01/23

For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled.

EXECUTIVE SUMMARY

Assessment of NP/SC 7813 Dungeness B Power Station - Initial Defuelling Safety Case, EC No: 369274 Revision 000

Permission Requested
In accordance with Dungeness B arrangements made under Licence Condition 22(1), EDF Nuclear Generation Limited (NGL) has requested the Office for Nuclear Regulation’s (ONR) Agreement to implement the Dungeness B Power Station Initial Defuelling Safety Case NP/SC 7813 EC No: 369274 Revision 000.

Background
In 2018 Dungeness B Power Station entered a double reactor outage to carry out remedial work on the plant. Due to a number of issues the reactors remained shutdown until June 2021 when NGL decided to move the station into the post operational phase. To enable fuel to be removed from the shutdown reactors the station has developed the Dungeness B Power Station Initial Defuelling Safety Case (IDSC) NP/SC 7813 to justify the safety of the initial defuelling operations.

Existing safety cases for routine off-load refuelling and reactor facilities already cover most of the handling operations required for defuelling. Two significant differences which are justified in the IDSC are:

Sealing defueled channels with an Empty Stringer Assembly (ESA). The ESA is similar to a standard fuel assembly but does not contain fuel pins. The ESA fits into the reactor and is laterally supported in a similar manner to a fuel assembly so drops of the assembly while in-situ. For example as a consequence of flow-induced vibration, can therefore be discounted. Installing the ESAs may affect the cooling pathways within the reactor.

Maintaining an adequate sub-critical margin (SCM). The reactors have met the existing shutdown margin (SDM) requirements since they ceased generation. However, removing fuel assemblies from the core, can if inadequately conceived, act to erode the margin to re criticality. This is referred to as the ‘subcritical margin’ (SCM). The ISDC will define the SCM criterion and demonstrate that an adequate level of SCM will be maintained throughout the defuelling.

Activities at the Irradiated Fuel Disposal Facility (IFDF), ponds and other fuel route facilities will be consistent with those employed during refuelling with the irradiated fuel being dispatched to Sellafield in flasks.

Assessment and inspection work carried out by ONR in consideration of this request
Before Dungeness B was moved into the post operational phase ONR had assessed and permissioned the implementation of the safety cases used for routine off-load refuelling and in other reactor facilities. The strategy adopted for this assessment was to take credit for the assessment and permissioning work already done by ONR and to carry out a proportionate and targeted assessment of the IDSC focussed on the new and novel aspects of the case.

# To deliver the assessment strategy ONR specialist inspectors in the disciplines listed below were asked to scope and carry out a proportionate and targeted assessment of the case.
- Structural Integrity
- Human Factors
- Fault Analysis (Fuel and Core)
- Fault Analysis (PSA)
- Fault Analysis
- Mechanical Engineering
- Electrical Engineering
- Control and Instrumentation
- Internal Hazards
- Chemistry
- Civil Engineering

The assessment also covered the adequacy of plant maintenance by considering engineering interventions carried out by ONR to assess the adequacy of pre defuelling maintenance work carried out on R21 and the regulatory oversight of safety justifications extending outage related maintenance intervals on R22.

Matters arising from ONR's work

The matters arising from the work carried out by ONR specialist are summarised as follows.

ONR specialist inspectors carried out proportionate and targeted assessment of the case in accordance with the strategy detailed above. The inspectors judged the IDSC to be an adequate safety case and supported a permissioning decision for ONR to agree to its implementation.

ONR engineering interventions during the R21 pre-defuelling outage found that maintenance was adequate, and no significant shortfalls were identified. On R22 the station extended the outage related maintenance intervals to May 2024 using its LC22 modifications arrangements and ONR has maintained appropriate oversight. This provides confidence the plant has been suitably maintained ready to commence defuelling.

Up to 16 fuel assemblies can be removed from the reactors and placed in Buffer Store 23 before being moved to the Irradiated Fuel Disposal Facility for disassembly. The integrity of the buffer stores cooling water circuit is important for nuclear safety as cooling is required for the irradiated fuel assemblies. The chemistry assessment identified a potential issue with corrosion in the towns water cooling circuit in Buffer Store 23. Corrosion is currently close to, but within the corrosion allowance. To maintain regulatory oversight of this issue a recommendation and regulatory issue have been raised to confirm the efficacy of the monitoring regime. This provides a suitable level of regulatory control and I judged that it was not proportionate to withhold agreement.

The safety case has been produced in accordance with NGL’s LC22 arrangements and has been verified, approved, and submitted to the Nuclear Safety Committee.

I have contacted the Dungeness B Environment Agency inspector and confirmed they have no reasons why ONR should withhold permission to implement the IDSC.

Conclusions
Based on the work carried out by ONR, I am satisfied that the Dungeness B Power Station Initial Defuelling Safety Case (IDSC) NP/SC 7813 EC No: 369274 Revision 000 is adequate safety case and can be implemented at Dungeness B Power Station to facilitate the start of defuelling the reactors.

Recommendations
I recommend that ONR should agree to the implementation of the NP/SC 7813 Dungeness B Power Station - Initial Defuelling Safety Case, EC No: 369274 Revision 000.

I also recommend ONR confirms commitments made in the ISDC relating to control rod isolation, boiler tube leak safety case and human factors integration to have been completed as planned before defuelling commences.

Given the small corrosion allowance remaining in buffer store 23 water jackets and decay tubes I recommend that to confirm the efficacy of the monitoring arrangements ONR should carry out an intervention to confirm Buffer Store 23 corrosion is within safety limits, prior to commencing of defuelling.
LIST OF ABBREVIATIONS

AC	Administrative Controls
AGR	Advance Gas Cooled Reactor
ALARP	As low as reasonably practicable
BSL	Basic Safety level (in SAPs)
BSO	Basic Safety Objective (in SAPs)
BTF	Boiler Tube Failure
DNB	Dungeness B
EC	Engineering Change (Modification)
EoG	End Of Generation
ESA	Empty Stringer Assembly
GCOT	Gas Circulator Outlet Temperature
HBSC	Human-Based Safety Claims
HEP	Human Error Probabilities
HF	Human Factors
HFI	Human Factors Integration
HOW2	(Office for Nuclear Regulation) Business Management System
HSE	The Health and Safety Executive
IAEA	The International Atomic Energy Agency
IDSC	Initial Defuelling Safety Case
IFDF	Irradiated Fuel Disposal Facility
NDA	Nuclear Decommissioning Authority
NGL	EDF Nuclear Generation Limited
NSP	Neutron Scatter Plugs
ONR	Office for Nuclear Regulation
OEM	Original Equipment Manufacture
PAR	Project Assessment Report
PSA	Probabilistic Safety Analysis
RGP	Relevant Good Practice
R21	Reactor 21
R22	Reactor 22
SAP	Safety Assessment Principle(s)
SCM	Sub-critical Margin
SDM	Shutdown Margin
SFAIRP	So far as is reasonably practicable
SSC	Structure, System and Component
TAG	Technical Assessment Guide (ONR)
TWC	Towns Water Cooling

TABLE OF CONTENTS

PERMISSION REQUESTED
In accordance with Dungeness B’s arrangements made under Licence Condition 22(1), EDF Nuclear Generation Limited (NGL) has requested [Ref 4] the Office for Nuclear Regulation’s (ONR’s) Agreement to implement the Dungeness B Power Station Initial Defuelling Safety Case (IDSC) NP/SC 7813 EC No: 369274 Revision 000 [Ref 5].
BACKGROUND
1. In 2018 Dungeness B Power Station entered a double reactor outage to carry out remedial work on the plant. Due to a number of issues the reactors remained shutdown until June 2021 when NGL decided to move the station into the post operational phase. To enable fuel to be removed from the shutdown reactors the station has developed the Dungeness B Power Station Initial Defuelling Safety Case (IDSC) NP/SC 7813 [Ref 5] to justify the safety of the initial defuelling operations.
2. Existing safety cases for routine off-load refuelling and reactor facilities already cover most of the handling operations required for defuelling. Returning of empty stringer assemblies (ESA) to the reactor is a significant new activity needed for defuelling and may affect the cooling pathways within the reactor. Another significant difference is the introduction in claim 2 to maintaining an adequate sub-critical margin (SCM). These are justified in the IDSC.
3. Activities at the Irradiated Fuel Disposal Facility (IFDF), ponds and other fuel route facilities will be consistent with those employed during refuelling with the irradiated fuel being dispatched to Sellafield in flasks.
4. There are a total of 408 channels to be defuelled in Reactor 21 (R21) and 407 in Reactor 22 (R22) (One vacancy following a dropped assembly in 1989). The IDSC covers removal of the first two hundred assemblies. The number taken from each reactor is not subject to individual limits. This limit approximates to the number of ESAs which can be assembled using the existing component stock. The initial defuelling safety case limit of 200 channels defueled provides time for further evaluation of other options for defuelling and to develop the full defuelling safety case which will justify the removal of the remaining fuel.
5. There are 38 new fuel assemblies present in the reactors which are expected to be returned to Springfields, subject to demonstration of acceptably low levels of contamination. Dismantling of this fuel will be undertaken at the New Fuel Facility rather than the Irradiated Fuel Disposal Facility (IFDF) under existing arrangements permitting these activities. If contamination levels are too high the fuel may need to be sent to Sellafield.
6. During defuelling the IDSC will be consistent with existing shutdown cooling and fuel handling arrangements. Where required the ISDC justifies any alternative arrangements which are required for defuelling. Fuel and ESA handling operations associated with defuelling will be carried out with a Gas Circulator Outlet Temperature (GCOT) between 160°C and 200°C at a minimum pressure in the range 230-260 psig. The lower temperature limit is increased to 160°C from the current pressurised refuelling limit of 76°C in support of core support integrity. The reactor decay heat is now very low and these defuelling temperatures will be achieved through heat input generated by high-speed operation of the gas circulators.
7. The case allows for defuelling of the two reactors to progress together. New fuel will be removed first and the completion of defuelling of one reactor will be sought before large scale defuelling of the other reactor takes place. There are 21 new fuel assemblies in R21 and 17 in R22, which will be removed before any irradiated fuel is removed from the respective reactors in order to maximise the SCM.
8. There are currently 165 fuel assemblies with original equipment manufacture (OEM) neutron scatter plugs (NSP) loaded in the two reactors. These NSPs have proved difficult to remove in the past and a safety case is being developed for their removal. The IDSC embargos the handling of OEM NSPs and their removal will be covered in the full defuelling safety case.
9. All control and safety group rods will be inserted into the core and isolated before defuelling commences contributing to maintaining the sub-critical margin in the reactor.
10. The station is producing implementation EC370477 and a readiness quality plan to control the activities and documentation changes needed for the implementation of the IDSC. It will include activities identified as prerequisites in the IDSC and any other lower tier activities as identified by station. Close-out of any remaining fuel route and shutdown reactor safety case issues carried over at the end of generation (EoG) is controlled and delivered separately as part of the ‘Post EoG Safety Case Programme’. ONR has engaged with this programme and identified the ECs where additional oversight was required.
11. The station has defined the entry point into the defuelling process as the point when the removal of a fuel assembly or fuel channel closure has commenced to enable the loading of the first Empty Stringer Assembly into either reactor. All operations undertaken before this entry point will continue to be justified under the existing refuelling and shutdown reactor safety cases.
1. ASSESSMENT AND INSPECTION WORK CARRIED OUT BY ONR IN CONSIDERATION OF THIS REQUEST
  1. Assessment Strategy
1. Before Dungeness B was moved into the post operational phase ONR had assessed and permissioned the implementation of the safety cases used for routine off-load refuelling and in other reactor facilities. These safety cases cover most of the fuel handling operations required for defuelling. The strategy adopted for this assessment was to take credit for the assessment and permissioning work already done by ONR on these cases and to carry out a proportionate and targeted assessment of the IDSC focussed on the new and novel aspects of the case. Individual specialist inspectors have scoped their assessments to sample the IDSC in accordance with this strategy.
2. The significant new activities covered by the IDSC and considered by the specialists in the assessment scopes are:
- In the defueled channels an Empty Stringer Assembly (ESA) will be used as a substitute for a new fuel stringer which would have been placed in the fuel channel during routine off-load refuelling. The ESA is similar to a new fuel assembly, but it does not contain any fuel pins. The ESA fits into the reactor and is laterally supported in a similar manner to a fuel assembly so drops of the assembly while in-situ. For example as a consequence of flow-induced vibration, can therefore be discounted. The use of the ESAs may affect the cooling pathways in the reactors, and this is included in the assessment.
- Maintaining an adequate sub-critical margin (SCM). The reactors have met the existing shutdown margin (SDM) requirements since they ceased generation. However, removing fuel assemblies from the core can if inadequately conceived, act to erode the margin to re criticality. This is referred to as the ‘subcritical margin’ (SCM). The ISDC will define the SCM criterion and demonstrate that an adequate level of SCM will be maintained throughout the defuelling.
- In 2017 Dungeness B identified a safety case anomaly and raised a JCO when it was identified that that continuing operation at power would significantly increase the frequencies for some categories of boiler tube failure (BTF) and that water from a boiler tube leak would pool in the gas circulator rather than gathering in the boiler annulus dead space as previously thought. A BTF safety case was developed in anticipation of a return to service, but this was never issued. BTF and associated water ingress remains a significant issue during defuelling, and a revised boiler tube failure safety case [Ref 6] was produced and is a reference in the IDSC. The assessment of the IDSC considers the adequacy of this BTF safety case.
To deliver the assessment strategy ONR specialist inspectors in the disciplines listed below were asked to scope and carry out a proportionate and targeted assessment of the case. A summary of each inspector’s assessment is given below and this forms the basis of the recommendations made in this Project Assessment Report (PAR).
- Structural Integrity
- Human Factors
- Fault Analysis (Fuel and Core)
- Fault Analysis (PSA)
- Fault Analysis
- Mechanical Engineering
- Electrical Engineering
- Control and Instrumentation
- Internal Hazards
- Chemistry
- Civil Engineering
  1. Structural Integrity
1. The Structural Integrity specialist inspector carried out an assessment of the IDSC [Ref 21].
2. The inspector primarily focused their assessment on sampling the structural integrity of systems, structures, and components (SSC) that are required to fulfil a nuclear safety function.
3. The inspector targeted the SSC which, in their opinion, are of most significance for nuclear safety and/or where the licensee proposed a change in the existing refuelling safety case. This is in accordance with ONR’s proportionality, accountability, consistency, targeted and transparent principles. In the safety case presented, and from a structural integrity perspective, the SSC are the metallic structures and components forming the reactor internals and boiler components. The inspector also considered the structural integrity justification for the graphite cores in the assessment.
4. Based on the evidence presented in the safety case, from the structural integrity viewpoint, the inspector concluded that:
- the licensee has undertaken a systematic assessment of the current condition of the structures and components, and their fitness for continued use for the duration of defuelling period.
- the licensee has provided adequate justification to support the assessment of degradation mechanisms of the SSC in the defuelling period.
- The return of the fuel plug unit to the reactor following discharge of the fuel elements introduces a new potential fault with the drop of a fuel plug unit (FPU) either during handling or whilst the fuel plug unit is stored in-situ in the reactor. The licensee has carried out an optioneering review and concluded that fitting empty stringer assemblies (ESAs) before returning the FPUs to the reactor is ALARP (as low as reasonably practicable). In the inspector’s opinion, the use of the ESAs significantly reduces the risk of dropping an FPU in situ and provides additional protection to the core support structure in the event of a drop during handling of the FPU. The licensee has, in the inspector’s view, provided adequate evidence to demonstrate that an FPU drop would not result in significant damage to the core support structure. In the inspector’s opinion, the use of ESAs is a suitable risk reduction measure.
1. From a structural integrity perspective, overall, the inspector was satisfied that there is adequate evidence to support the Licensee’s claims and arguments presented in the initial defuelling safety case NP/SC 7813.
2. The inspector concluded that from a structural integrity perspective, they recommend the release of the LC22 agreement licence instrument to allow initial defuelling at DNB under safety case NP/SC 7813.
  1. Human Factors Assessment
1. The Human Factors (HF) specialist inspector carried out an assessment of the IDSC [Ref 28].
2. The inspector focussed on the removal and export of nuclear fuel assemblies, maintaining the SCM by compliance with the defuel plan, and the building and loading of ESAs. The inspector did not assess elements that are either unchanged from, or bounded by, existing safety cases.
3. In support of the IDSC, NGL have defined, and are in the process of completing a programme of work to integrate human factors considerations within the case and the associated arrangements necessary for its implementation. To date NGL has completed sufficient work to adequately understand the operator contribution to nuclear safety and integrate human factors considerations into the design and safety case, including:
- review of the extant substantiations of a sample of risk significant refuelling human-based safety claims (HBSCs);
- review of new or modified administrative controls (ACs) identified in the IDSC;
- detailed qualitative analysis of mis-load and mis-defuel faults; and
- initial substantiation of Human Error Probabilities (HEPs), including some derived from other AGRs, required to support the probabilistic safety assessment (PSA).
1. Based on the evidence presented, the inspector’s assessment concurs with NGL’s conclusions that the body of work completed to date is sufficient to provide confidence that, assuming robust implementation, the IDSC demonstrates risk arising from human error during defuelling is reduced so far as is reasonably practical (SFAIRP).
2. The inspector judged that sufficient progress has been made to support the request for agreement to implement the IDSC given NGL’s commitment to complete its HFI programme, close out recommendations, validate current assumptions and fully substantiate the HBSCs required to underpin the case. The inspector recommended that from a human factors perspective, they supported the release of the Licence Instrument agreeing to the implementation of the IDSC.
3. To ensure the human factors integration and justifications are completed satisfactorily the inspector made the following recommendations which have been taken forward in this PAR and actioned in regulatory issue RI-11114.
- NGL should provide ONR with suitable evidence demonstrating closure of all human factors-related recommendations and action requests, prior to the ONR readiness inspection.
- NGL to provide ONR with suitable evidence that it has validated human factors assumptions made in the IDSC, confirmed the absence of error producing conditions and performance shaping factors which have the potential to significantly impact human performance and collated appropriate human factors substantiation evidence demonstrating risks arising from human error are as low as reasonably practicable.
- ONR should inspect the adequacy of NGL’s arrangements implementing the IDSC during its inspection of readiness. This should include, but not necessary be limited to, consideration of compliance with licence conditions 10, 12, 23 and 24. The involvement of the ONR Human Factors inspector should be considered.
  1. Fault analysis (fuel and core)
1. The Fault Studies (Fuel & Core) specialist inspector carried out an assessment of the IDSC [Ref 19].
2. The inspector was satisfied the claims, arguments and evidence laid down within EDF NGL’s safety case demonstrate that the risks associated with the proposal are ALARP, from a Fuel and Core perspective. They found that:
- the fundamental safety functions – control of reactivity, removal of heat from the fuel and confinement of radioactive material – will be delivered with an appropriate degree of confidence;
- the PANTHER core analysis code is suitable for the applications to which it has been put and uncertainties in the supporting nuclear data have been addressed in a suitable way;
- the chosen defuel order will reduce risks to ALARP; and
- the non-preferred option in the IDSC to discharge new fuel through the IFDF and ponds to Sellafield (if it cannot be sent to Springfields) does not yet appear to be available at the time of writing. However, the inspector judged that this issue should not prevent permissioning of the IDSC because there is a safety benefit to removing the new fuel from the reactor early. EDF has a means to store the fuel if necessary until it can be consigned off-site and it has adequate radiological protection arrangements in place.
The inspector recommended that the ONR Project Inspector provides Agreement for EDF to proceed with the Initial Defuelling Safety Case for Dungeness B (NP/SC 7813) as presented in EC 369274.
  1. Fault Analysis (PSA)
1. The PSA Fault Studies specialist inspector carried out an assessment of the IDSC [Ref 20]. They concluded:
2. While the Initial Defuelling Safety Case includes both the shutdown reactor and fuel handling safety case, it does not use PSA to support the safety case of the shutdown reactor. Whilst this does not meet modern standards expectations for scope of PSA, given the reducing risk levels and the historical context of PSA development for the advanced gas cooled reactors the inspector did not consider this shortfall to be of sufficient significance to prevent a license instrument being granted from a PSA perspective.
3. A defuelling PSA has been developed to support the Initial Defuelling Safety Case. The inspector assessed the Initial Defuelling Safety Case by sampling the areas related to PSA, focusing on sufficient use of PSA and probabilistic insights, the adequacy of the probabilistic claims made, comparison against numerical targets and a judgement on if risks have been reduced ALARP .
4. The defuelling PSA is an updated version of the refuelling PSA which ensures the scope and level of detail of the defuelling PSA is comparable to that of the extant refuelling PSA, whilst leading to some conservatism related to grace times for operator actions during different handling operations.
5. Additional faults have been added to the PSA related to mis-loading and mis‑defuelling of the reactor and drop of an empty stringer assembly. The inspector assessed these faults on a sampling basis and is satisfied with the PSA has been used to inform the safety case.
6. Further work is committed to by EDF Nuclear Generation Limited to fully substantiate some operator actions within the defuelling PSA prior to defuelling commencing. Following discussions with the human factors inspector the inspector was satisfied that the follow up work committed to by EDF is appropriate and that the risks will be bounded by PSA sensitivity studies produced by EDF.
7. The inspector was satisfied with the adequacy and use of PSA and probabilistic insights within the licensee's safety case and that defuelling risks have been reduced ALARP from a PSA perspective. The overall risk of defuelling is lower than the risk from refuelling, and defuelling will move the station to a safer state.
8. The inspector was satisfied with the claims, arguments and evidence laid down within EDF’s EC NP/SC 7813 Dungeness B Initial Defuelling Safety Case. They judged that the proposal is adequate from a PSA perspective to justify the issue of a Licence Instrument for ONR’s Agreement under arrangements made under Licence Condition 22.
  1. Fault analysis
1. The Fault Studies specialist inspector carried out an assessment of the IDSC [Ref 18].
2. The inspector carried out a targeted and proportionate regulatory assessment of the fault studies aspects of the DNB IDSC which focused on the postulated new faults with potential to occur during defuelling, and existing faults, such as BTF , for which the risk remains significant under the defuelling operations.
3. The inspector concluded that the DNB initial defuelling safety case adequately demonstrates that the risks associated with the proposed defuelling activities are reduced ALARP .
4. The conclusion is based on the following assessment findings:
- The inspector was satisfied that the credible faults associated with the proposed defuelling operations have been identified in a systematic, auditable, comprehensive manner.
- The inspector was content that NGL has undertaken adequate safety analyses to provide a robust demonstration of fault tolerance of the engineering design and the effectiveness of the safety measures by using appropriate codes and methods.
- The inspector judged that due to the significant reduction in reactor core decay heat after the shut-down for over three years, the safety margins have increased considerably. Therefore, longer post-accident recovery time is available to allow the operators to identify the faults and take appropriate recovery actions to mitigate the consequence.
NGL made the following commitments to update EC370308 Revision 000 [Ref 6] to Revision 001 to
- develop a robust boiler management to underwrite the integrity of the main boiler and reheaters until the end of defuelling operations;
- provide a comprehensive justification of water ingress risk during defuelling phase of operating, ensuring that the management and operation of the boilers is consistent with a level of risk that is ALARP;
- enhance boiler tube failure identification capabilities;
- implement an EC to mitigate the potential for boiler tube failure following a demand for feed from Additional Feed System (AFS).
1. The inspector judged the BTF safety case as adequate to support the claims made in IDSC, provided that the commitments above have been fulfilled and achieve their defined objectives. The inspector therefore recommended ONR considers requesting EC370308 Revision 01 for review when it is available to ensure that the commitments made in EC370308 Revision 00 are delivered. This is taken forward as a recommendation in this PAR.
2. From a fault studies perspective, based on the sample taken, the inspector recommended ONR release the LC22 Agreement Licence Instrument to allow NGL to proceed the proposed defuelling activities.
  1. Mechanical engineering
1. The Mechanical Engineering specialist inspector carried out an assessment of the IDSC [Ref 25].
2. The inspector’s assessment sampled the following mechanical engineering aspects, which they considered important to nuclear safety:
- The adequacy of examination, inspection, maintenance and testing requirements for mechanical equipment used in fuel handling and dismantling.
- The adequacy of lifting integrity over the stations initial defuelling period.
1. From a mechanical engineering perspective, the inspector judged that NGL has demonstrated the risks associated with the activities to be undertaken as part of initial defuelling operations at Dungeness B are bounded by the extant refuelling safety cases.
2. From a mechanical engineering perspective, the inspector recommended the release of the LC22 agreement licence instrument to allow defuelling of up to 200 channels at Dungeness B power station under the operational conditions given within the Initial Defuelling Safety Case.
  1. Electrical engineering
1. The IDSC was reviewed [Ref 9] by an electrical engineering specialist inspector and it was not considered proportionate to carry out a full assessment of the case due to its similarity to the existing safety cases. One key part of the case considered was the isolation of the control rods which forms part of the justification for maintaining an adequate sub critical margin.
2. From an electrical engineering perspective, the inspector considered that a control rod withdrawal fault will not be credible, if the control rods, including the safety group, will be inserted prior to the start of defueling and the electrical supplies to all control rod drives are permanently and securely isolated and it is positively confirmed that all control rods cannot be withdrawn, as described within EC 370400 [Ref 10]. As the implementation of EC 370400 [ref 10] is subject to DNB receiving an agreement from ONR on its assessment of the IDSC, the inspector made the following recommendation which is taken forward as a recommendation of this PAR.
3. Recommendation - EDF should not commence defueling at Dungeness B, in accordance with the initial defueling safety case EC 369274, until ONR has conducted an intervention. This is to verify from a sample that all control rods have been inserted and the electrical supplies to all control rod drives are permanently and securely isolated, in accordance with EC 370400, and it has been positively confirmed that all control rods cannot be electrically withdrawn.
4. The specialist concluded that they were satisfied with the claims arguments and evidence provided within the IDSC and did not identify anything else of safety significance in relation to electrical engineering aspects that should prevent the implementation of the IDSC. The specialist therefore recommended ONR gives Agreement to the implement the DNB IDSC.
  1. civil engineering
1. The Civil Engineering specialist inspector carried out a review of the IDSC [Ref 22].
2. The inspector selected a limited sampled of four main areas with relevance to civil engineering aspects of the safety case including a high-level review of some of the claims, arguments, and evidence relevant to civil engineering. The inspector did not consider the civil aspects were key to the safety justification or permissioning decision, so a full assessment was not considered proportionate.
3. The inspector concluded is that no immediate concerns were highlighted within the review relating to the civil engineering aspects sampled. They were satisfied with the claims, arguments and evidence laid down within the safety case.
4. The inspector recommended that agreement should not be unduly withheld in relation to the civil engineering aspects.
  1. control & instrumentation
1. The Control and Instrumentation specialist inspector carried out a review of the IDSC [Ref 23].
2. The Inspector considered:
- the impact of handling the lighter empty stringer assemblies, particularly with regards to dropped load protection and load trips.
- control rod isolation, including control rod position indications.
- redundant C&I systems.
- performance of C&I systems retained on the shutdown reactors.
- C&I protection against dropped flask faults.
The inspector judged the C&I aspects of the IDSC to be adequate and recommended that ONR’s Project Inspector gives Agreement to the LC22 request by EDF NGL to implement the IDSC.
  1. Internal Hazards
1. The Internal Hazards specialist inspector carried out a review of the IDSC [Ref 24].
2. The internal hazards assessment scope took into consideration ONR’s assessments of defuelling campaigns at other Advanced Gas Cooled Reactor (AGR) sites and has specifically focussed on the differences or novel aspects of the DNB defuelling campaign versus such previous campaigns. Primarily this covers NGL’s decision to undertake defuelling of the reactor in a warm and pressurised state, the decision to seal empty channels with ESAs and the potential de-classification of safety systems usually employed as part of the operational or refuelling safety cases currently in place.
3. The assessment concluded that internal hazards aspects have been adequately considered and managed within the existing interfacing safety case and the IDSC. The assessment therefore supports the issuing of a licence instrument to permission the above activities.
  1. Chemistry
1. The Chemistry specialist inspector carried out a review of the IDSC [Ref 27].
2. The inspector noted the defueling operations will be carried out with the reactor warm and pressurised. This is consistent with the assumptions of the current refuelling safety case. Their assessment focussed on: primary gas chemistry (including carbon deposition), ponds chemistry and ancillary systems chemistry.
3. The inspector noted that references in the IDSC show corrosion in the buffer store 23 towns water cooling (TWC) water jackets and decay tubes has been assessed to be between 1.33 and 1.62mm out of a corrosion limit of 1.75mm. NGL estimates that if the use of Buffer Store 23 continues to 2028, there is a risk of this corrosion allowance being exceeded. The integrity of the cooling water circuit is important for nuclear safety as cooling is needed for the irradiated fuel held in the buffer store to prevent a radiological release. NGL makes a commitment in the IDSC to begin three yearly reviews of TWC chemistry control and vault air conditioning unit operation in 2022 to ensure corrosion allowances are not exceeded. The 2022 review had not been completed at the time of writing this PAR. The inspector has accepted NGL’s conclusion that water jackets are currently within the corrosion allowance but given the small corrosion allowance remaining the inspector recommends that to confirm the efficacy of the corrosion monitoring arrangements ONR should carry out an intervention to confirm Buffer Store 23 corrosion is within safety limits, prior to commencing of defuelling. The inspector has raised a level 4 regulatory issue (RI 11100) to track the intervention.
4. The inspector concluded they were content with the claims, arguments and evidence laid down within the Licensee’s safety case and recommend ONR does not object to the activity from a chemistry perspective.
  1. EDF Safety Case Process
I have confirmed that the NGL processes for producing, verifying and independent nuclear safety assessment have been followed and that the IDSC has been presented to the NSC. The INSA Certificate and Comments have been provided to ONR [Ref 7] and have been considered, as necessary, in the specialist assessments. NGL have also provided the Nuclear Safety Committee (NSC) meeting minutes [Ref 8] which record the discussion of the of the IDSC. The committee offered no advice but asked the case officer to consider two items. The case officer has done this and reported back to the NSC. I am therefore satisfied the safety case approval process was adhered to and appropriate safety barriers were in place.
  1. Dungeness B ONR Engineering Interventions.
1. In 2022 Dungeness B undertook a pre-defuelling outage on Reactor 21 to carry out plant maintenance schedule (PMS) activities and prepare for defuelling. ONR engineering specialists carried out licence condition 28 (Examination, inspection, maintenance and testing) inspections which found the maintenance was adequate and no significant shortfalls were identified. The inspections were rated green against ONR rating criteria. This provided confidence the plant on R21 will be in a suitable condition to commence defuelling. The intervention reports are: Electrical Engineering [Ref 11], Control and Instrumentation [Ref 12], Mechanical Engineering [Ref 13] and Structural Integrity [Ref 14].
2. Reactor 22’s last statutory outage was nominally completed by 31 December 2018 and the PMS identifies the interval for items being maintained during outage as three years (or multiples of) meaning maintenance of these items fell due on 31 December 2021. The reactor has not operated at power since this outage and Dungeness B produced an EC to justify extending the outage related maintenance intervals up to 31 May 2023. ONR decided to request the EC ‘for information’ and this is recorded in a DR [Ref 15].
3. Dungeness intends to further extend the outage related maintenance activities on R22 to May 2024. This period may include some defuelling of the reactor and ONR has received the EC justifying safety for ‘review and consideration’ so a suitable level of regulatory control is maintained. This is recorded in a decision record [Ref 16].
4. A Civil Engineering Inspector visited Dungeness B to discuss the Pre-Stressed Concrete Pressure Vessel (PCPV) PSSR competent persons examinations and management of site infrastructure and no shortfall were recorded. [Ref 17].
5. ONR has therefore carried out interventions to confirm the efficacy of the pre-defuelling outage maintenance activities carried out on R21 and is exerting a suitable level of regulatory oversight and control over the ECs which provide the safety justifications for extending maintenance intervals on R22. Therefore, I consider there are no issues regarding plant maintenance which preclude ONR agreement to the implementation of the IDSC.
MATTERS ARISING FROM ONR’S WORK
1. The matters arising from the work carried out by ONR specialist are summarised as follows.
2. ONR specialist inspectors carried out proportionate and targeted assessment of the case in accordance with the strategy detailed above. The inspectors judged the IDSC to be an adequate safety case and supported a permissioning decision for ONR to agree to its implementation. Recommendations made in the individual assessment reports have been addressed in the relevant paragraphs above and carried forward as recommendations in this PAR.
3. ONR engineering interventions during the R21 pre-defuelling outage found that maintenance was adequate, and no significant shortfalls were identified. On R22 the station extended the outage related maintenance intervals to May 2024 using its LC22 modifications arrangements and ONR has maintain appropriate oversight. This provides confidence the plant has been suitably maintained ready to commence defuelling.
4. The chemistry assessment identified a potential issue with corrosion in the Buffer Store 23 TWC system. The corrosion is currently close to but within the corrosion allowance. To maintain regulatory oversight of this issue a recommendation and regulatory issue (RI 11100) have been raised to confirm the efficacy of the monitoring regime. This provides a suitable level of regulatory control and I judged that it was not proportionate to withhold agreement.
5. The safety case has been produced in accordance with NGL’s LC22 arrangements and has been verified, approved and submitted to the Nuclear Safety Committee.
6. I have contacted the Dungeness B Environment Agency Inspector and confirmed they have no reasons why ONR should withhold permission to implement the IDSC. [Ref 26].
CONCLUSIONS
1. Based on the work carried out by ONR, I am satisfied that the Dungeness B Power Station Initial Defuelling Safety Case (IDSC) NP/SC 7813 EC No: 369274 Revision 000 is adequate safety case and can be implemented at Dungeness B Power Station to facilitate the start of defuelling the reactors.
2. Where the specialist inspectors made recommendations, they have been carried forward as recommendations in this PAR.
RECOMMENDATIONS
1. I recommend that ONR should agree to the implementation of the NP/SC 7813 Dungeness B Power Station - Initial Defuelling Safety Case, EC No: 369274 Revision 000 and I have prepared licence instrument 568 for signature.
2. The safety case will be permissioned a number of months before defuelling begins and it contains a number of activities and commitments which must be completed before defuelling commences. Based on the assessment findings I therefore also recommend the following and have raised regulatory issue RI-11114 to track to close out:
- ONR should request the Shutdown Cooling Boiler Tube Failure Safety Case EC370308 Revision 01 for review when it is available to ensure that the commitments made in EC370308 Revision 00 [Ref 6] are delivered adequately.
- NGL should not commence defueling at Dungeness B, in accordance with the initial defueling safety case EC 369274, until ONR has conducted an intervention to verify from a sample that all control rods have been inserted and the electrical supplies to all control rod drives are permanently and securely isolated, in accordance with EC 370400, and it has been positively confirmed that all control rods cannot be electrically withdrawn.
- Before Dungeness B commences defuelling ONR should carry out an intervention to confirm that all human factors-related commitments, recommendations, and action requests associated with the IDSC have been completed as planned.
- Before Dungeness B commences defuelling ONR should carry out an intervention to assess the adequacy of the arrangements that implement the IDSC. The scope should include consideration of licence conditions 10, 12, 23 and 24. The involvement of the ONR Human Factors Inspector should be considered.
Given the small corrosion allowance remaining in buffer store 23 water jackets and decay tubes I recommend that to confirm the efficacy of the monitoring arrangements ONR should carry out an intervention to confirm Buffer Store 23 corrosion is within safety limits, prior to commencing of defuelling. The Chemistry Specialist inspector has raised a level 4 regulatory issue (RI 11100) to track this issue.
REFERENCES
ONR Guide – The Purpose and Use of Permissioning - NS-PER-GD-001 Revision 6. October 2022. http://www.onr.org.uk/operational/assessment/index.htm
Safety Assessment Principles for Nuclear Facilities. 2014 Edition, Revision 1. January 2020. http://www.onr.org.uk/saps/saps2014.pdf.
TAGs http://www.onr.org.uk/operational/tech_asst_guides/index.htm
Dungeness B Letter NSLDNB50109R – NP/SC 7813 Rev 000 Initial Defuelling Safety Case EC 369274, 31 August 2022, CM9 2022/51277
Dungeness B Power Station Initial Defuelling Safety Case (IDSC) NP/SC 7813 EC No: 369274 Revision 000. August 2022, CM9 2022/51278
Dungeness B - EC 370308 Revision 000 - Shutdown Cooling Boiler Tube Failure Safety Case, CM9 2022/38837
Full INSA Approval Statement Initial Defuelling Safety Case NP/SC 7813 EC No./Rev No.:369274/000, Version No.:03, CM9 2022/56873
Dungeness B and Sizewell B Nuclear Safety Committees, Minutes of the Meeting Held at Dungeness B on 16th August 2022, 31 August 2022, CM9 2022/51211
Electrical Engineering Assessment of DNB Initial Defuelling Safety Case (IDSC), e-mail, 31 October 2022, CM9 2022/63104
EC 370400 Revision 0 Version 0 Isolation of Control rods in Support of the Dungeness B Initial Defueling Safety Case, CM9 2022/56141
ONR-OFD-IR-22-010 Revision No.: 0, EDF Energy Nuclear Generation Limited – Dungeness B power station defueling aspirations intervention – Licence condition 28 inspection of electrical engineering related aspects. CM9 2022/30004
ONR-OFD-IR-22-028 Revision No. 000, EDF Energy Nuclear Generation Ltd (EDF NGL) – Dungeness B (DNB) Power Station, R21 Pre-Defuelling Outage (019) and Fuel Route Outage Control and Instrumentation (C&I) Inspection, CM9 2022/37528
ONR-OFD-IR-22-046 Revision No. 0, Dungeness B Reactor 21 Outage 019 – Mechanical Engineering Inspection, CM9 2022/45549
ONR-OFD-IR-22-009 Revision No. 0, Dungeness B Power Station - Reactor 21 - LC28 Inspection of Structural Integrity Related Pre-Defueling Maintenance and Examination Activities, CM9 2022/28083
ONR-OFD-DR-21-043, Dungeness B Reactor 22: Proposal to Defer Reactor 22 Outage 022 Following The 2018-2021 Double Reactor Outage EC Number: 369119 000, CM9 2021/71679
ONR-OFD-DR-22-013 EC 369119 Revision 001, Extending Maintenance Intervals R22 to March 2024, EC 369119 Revision 001, CM9 2022/55157
ONR-OFD-CR-22-174 Civil Engineering Site Visit to Dungeness B to Discuss PCPV Examinations and Management of Site Infrastructure, CM9 2022/35236
ONR-OFD-AR-22-028 Fault Studies Assessment – Initial Defuelling Safety Case NP/SC 7813, November 2022, CM9 2022/63211
ONR-OFD-AR-22-033 NP/SC 7813, Dungeness B Power Station Initial Defuelling Safety Case (EC 369274), November 2022, CM9 2022/57987
ONR-OFD-AR-22-043 Dungeness B Initial Defuelling Safety Case Probabilistic Safety Analysis Specialist Assessment, November 2022, CM9 2022/62714
ONR-OFD-AR-22-027 Consideration of the Structural Integrity Aspects of the Dungeness B Initial Safety Case NP/SC 7813, November 2022, CM9 2022/60094
ONR-OFD-AR-22-046 Issue D, NP/SC 7813 rev 000 Initial de-fuelling safety case Civil engineering report in relation to request for Agreement under Arrangements made under Licence Condition 22(1), November 2022, CM9 2022/68546
ONR-OFD-AR-22-042, Dungeness B Initial Defuelling Safety Case EC 369274 Control and Instrumentation Assessment of EDFNGL Dungeness B Initial Defuelling Safety Case EC 369274, November 2022, CM9 2022/64915
ONR-OFD-AR-22-050 Dungeness B Power Station Initial Defuelling Safety Case – Internal Hazards Assessment, November 2022, CM 9 2022/69162
Unique Doc. ID: 2022/65511 - Mechanical engineering assessment of the Dungeness B Initial Defuelling Safety Case – NP/SC 7813, November 2022, CM9 2022/65511
Environment Agency E-mail, 04 October 2022, CM9 2022/57477
ONR-OFD-AR-22-044 Chemistry Assessment of NP/SC 7813 NP/SC 7813 Dungeness B Power Station: Initial Defueling Case, November 2022, CM9 2022/54778
ONR-OFD-AR-22-054 Human Factors Assessment of NP/SC 7813 NP/SC 7813, Dungeness B Power Station Initial Defuelling Safety Case (EC 369274), December 2022, CM9 2022/65592